## Sheet1
Device Name: basler_dgc2020
Available Template Part number |  | Description
Basler_DGC2020_T28 |  | Modbus RTU to BACnet MS/TP
Basler_DGC2020_T29 |  | Modbus RTU to BACnet/IP
Basler_DGC2020_T1110 |  | Modbus RTU to Allen-Bradley PLC
Basler_DGC2020_T486 |  | Modbus TCP/IP to BACnet/IP
Basler_DGC2020_T487 |  | Modbus TCP/IP to BACnet MS/TP
Basler_DGC2020_T1111 |  | Modbus TCP/IP to Allen-Bradley PLC
Point | Point Name
1 | Generator PT Primary Voltage
2 | Generator PT Secondary Voltage
3 | Generator CT Primary Current
4 | Low Fuel Alarm Enable
5 | Low Fuel Alarm Threshold
6 | Low Fuel Pre-Alarm Enable
7 | Low Fuel Pre-Alarm Threshold
8 | Low Coolant Temp PA Enable
9 | Low Coolant Temp PA Threshold
10 | Battery Overvoltage PA Enable
11 | Reserved
12 | Maintenance Interval PA Enable
13 | Maintenance Interval PA Threshol
14 | Engine KW Overload PA Enable
15 | Engine KW Overload PA Threshold
16 | High Coolant Temp PA Enable
17 | High Coolant Temp PA Thresh
18 | Low Oil Pressure PA Enable
19 | Low Oil Pressure PA Threshold
20 | Low Battery Voltage PA Enable
21 | Low Battery Voltage PA Threshold
22 | Low Battery Voltage PA Time Dly
23 | Weak Battery Voltage PA Enable
24 | Weak Battery Voltag PA Threshold
25 | Weak Battery Voltage PA Time Dly
26 | High Coolant Temp Alarm Enable
27 | High Coolant Temp Alarm Threshol
28 | High Cool Temp Alarm Arming Dly
29 | Low Oil Pressure Alarm Enable
30 | Low Oil Pressure Alarm Threshold
31 | Low Oil Pressur Alarm Arming Dly
32 | Overspeed Alarm Enable
33 | Overspeed Alarm Threshold
34 | Overspeed Alarm Activation Dly
35 | RMS Voltage A-B
36 | RMS Voltage B-C
37 | RMS Voltage C-A
38 | RMS Voltage A-N
39 | RMS Voltage B-N
40 | RMS Voltage C-N
41 | RMS Current Phase A
42 | RMS Current Phase B
43 | RMS Current Phase C
44 | Apparent Power Phase A
45 | Apparent Power Phase B
46 | Apparent Power Phase C
47 | Apparent Power 3-Phase
48 | Power Phase A
49 | Power Phase B
50 | Power Phase C
51 | Power 3-Phase
52 | Power Factor
53 | Frequency
54 | Generator Speed Mode
55 | Power Factor State
56 | Input Contacts States
57 | BESTCOMS Test Buttons States
58 | Accelerator Pedal Position
59 | % Load At Current Speed
60 | Actual Engine % Torque
61 | Engine Speed
62 | Injection Control Pressure2
63 | Injector Metering Rail Pressure2
64 | Engine Run Time 1
65 | Engine Run Time 2
66 | Engine Run Time 3
67 | Trip Fuel 1
68 | Trip Fuel 2
69 | Trip Fuel 3
70 | Total Fuel Used 1
71 | Total Fuel Used 2
72 | Total Fuel Used 3
73 | Coolant Temp
74 | Fuel Temp
75 | Engine Oil Temp
76 | Engine Intercooler Temp
77 | Fuel Delivery Pressure
78 | Engine Oil Level
79 | Oil Pressure
80 | Coolant Pressure
81 | Coolant Level
82 | Fuel Rate
83 | Barometric Pressure
84 | Ambient Air Temp
85 | Air Inlet Temp
86 | Boost Pressure
87 | Intake Manifold Temp
88 | Air Filter Diff Pressure
89 | Exhaust Gas Temp
90 | Electrical Potential Voltage
91 | Batt Potential Volt Switched
92 | Speed At Idle Point1
93 | Torque At Idle Point1
94 | Speed At Idle Point2
95 | Torque At Idle Point2
96 | Speed At Idle Point3
97 | Torque At Idle Point3
98 | Speed At Idle Point4
99 | Torque At Idle Point4
100 | Speed At Idle Point5
101 | Torque At Idle Point5
102 | Speed At High Idle Point6
103 | Gain of End Speed Governor
104 | Reference Engine Torque
105 | Override Speed Point7
106 | Override Time Limit
107 | Speed Lower Limit
108 | Speed Upper Limit
109 | Torque Lower Limit
110 | Torque Upper Limit
111 | Crankcase Pressure
112 | Oil Filter Diff Pressure
113 | Fuel Filter Diff Pressure
114 | Gen VAB Metering
115 | Gen VBC Metering
116 | Gen VCA Metering
117 | Gen VAN Metering
118 | Gen VBN Metering
119 | Gen VCN Metering
120 | Bus Voltage Metering
121 | Gen IA Metering
122 | Gen IB Metering
123 | Gen IC Metering
124 | Gen kVA A Metering
125 | Gen kVA B Metering
126 | Gen kVA C Metering
127 | Gen kVA Total Metering
128 | Gen kW A Metering
129 | Gen kW B Metering
130 | Gen kW C Metering
131 | Gen kW Total Metering
132 | Power Factor Metering
133 | Gen PF Lagging
134 | Gen Frequency Metering
135 | Bus Frequency Metering
136 | Active Speed Source
137 | Engine Speed Metering
138 | Engine Load Metering
139 | Coolant Temp Metering
140 | Oil Pressure Metering
141 | Battery Voltage Metering
142 | Fuel Level Metering
143 | ECU Coolant Level Metering
144 | Cool Down Time Remaining
145 | Alarm Metering
146 | Pre-Alarm Metering
147 | MDEC Alarm Metering
148 | MDEC Pre-Alarm Metering
149 | Sender Fail Alarm Metering
150 | Protection Alarm Metering
151 | Reserved
152 | Reserved
153 | Local Input Metering
154 | Local Output Metering
155 | Status Metering

## Overall (hidden)
Read / Write
None
Read
Write
Read/Write

## Protocol_Selection (hidden)
Protocol 1 Selection | Protocol 2 Selection
Modbus RTU Master (MM) | BACnet/IP Server (BS)
Modbus TCP/IP Client (MC) | BACnet MS/TP Slave (BMS)

## Mapping (hidden)
Manipulation
None
Mult by 10.0
Mult by 100.0
Mult by 1000.0
Mult by 10000.0
Div by 10.0
Div by 100.0
Div by 1000.0
Div by 10000.0
Extract Bit 0
Extract Bit 1
Extract Bit 2
Extract Bit 3
Extract Bit 4
Extract Bit 5
Extract Bit 6
Extract Bit 7
Extract Bit 8
Extract Bit 9
Extract Bit 10
Extract Bit 11
Extract Bit 12
Extract Bit 13
Extract Bit 14
Extract Bit 15
Extract Bit 16
Extract Bit 17
Extract Bit 18
Extract Bit 19
Extract Bit 20
Extract Bit 21
Extract Bit 22
Extract Bit 23
Extract Bit 24
Extract Bit 25
Extract Bit 26
Extract Bit 27
Extract Bit 28
Extract Bit 29
Extract Bit 30
Extract Bit 31
Extract Bit 32
Extract Bit 33
Extract Bit 34
Extract Bit 35
Extract Bit 36
Extract Bit 37
Extract Bit 38
Extract Bit 39
Extract Bit 40
Extract Bit 41
Extract Bit 42
Extract Bit 43
Extract Bit 44
Extract Bit 45
Extract Bit 46
Extract Bit 47
Extract Bit 48
Extract Bit 49
Extract Bit 50
Extract Bit 51
Extract Bit 52
Extract Bit 53
Extract Bit 54
Extract Bit 55
Extract Bit 56
Extract Bit 57
Extract Bit 58
Extract Bit 59
Extract Bit 60
Extract Bit 61
Extract Bit 62
Extract Bit 63

## Modbus_Configuration (hidden)
Modbus Data Types | Modbus Read Data Types | Modbus Write Data Types | Max Address per Request by Data Type
0x Coil Status (Bit) | 0x Coil Status (Bit) | 0x Coil Status (Bit) | 512
1x Input Status (Bit) | 1x Input Status (Bit) | 4x Holding Register (16 Bit Int) | 125
3x Input Register (16 Bit Int) | 3x Input Register (16 Bit Int) | 4x Holding Register (16 Bit Uint) | 125
3x Input Register (16 Bit Uint) | 3x Input Register (16 Bit Uint) | 4x Holding Register (32 Bit Int) | 62
3x Input Register (32 Bit Int) | 3x Input Register (32 Bit Int) | 4x Holding Register (32 Bit Uint) | 31
3x Input Register (32 Bit Uint) | 3x Input Register (32 Bit Uint) | 4x Holding Register (32 Bit Float)
3x Input Register (32 Bit Float) | 3x Input Register (32 Bit Float) | 4x Holding Register (64 Bit Int)
3x Input Register (64 Bit Int) | 3x Input Register (64 Bit Int) | 4x Holding Register (64 Bit Uint)
3x Input Register (64 Bit Uint) | 3x Input Register (64 Bit Uint) | 4x Holding Register (64 Bit Float)
3x Input Register (64 Bit Float) | 3x Input Register (64 Bit Float)
4x Holding Register (16 Bit Int) | 4x Holding Register (16 Bit Int)
4x Holding Register (16 Bit Uint) | 4x Holding Register (16 Bit Uint)
4x Holding Register (32 Bit Int) | 4x Holding Register (32 Bit Int)
4x Holding Register (32 Bit Uint) | 4x Holding Register (32 Bit Uint)
4x Holding Register (32 Bit Float) | 4x Holding Register (32 Bit Float)
4x Holding Register (64 Bit Int) | 4x Holding Register (64 Bit Int)
4x Holding Register (64 Bit Uint) | 4x Holding Register (64 Bit Uint)
4x Holding Register (64 Bit Float) | 4x Holding Register (64 Bit Float)

## BACnet_Configuration (hidden)
BACnet Object Types | BACnet Read Object Types | BACnet Write Object Types | BACnet Units
Analog Input | Analog Input | Analog Output | %/s: (percent-per-second)
Analog Output | Binary Input | Binary Output | %obs/ft: (percent-obscuration-per-foot)
Binary Input | Character String Value | Character String Value | %obs/m: (percent-obscuration-per-meter)
Binary Output |  |  | /h: (per-hour)
Character String Value |  |  | ang: (degrees-angular)
C/h: (degrees-Celsius-per-hour)
C/m: (degrees-Celsius-per-minute)
C: (degrees-Celsius)
F/h: (degrees-Fahrenheit-per-hour)
F/m: (degrees-Fahrenheit-per-minute)
F: (degrees-Fahrenheit)
K/h: (degrees-Kelvin-per-hour)
K/m: (degrees-Kelvin-per-minute)
K: (degrees-Kelvin)
phase: (degrees-phase)
A/m: (amperes-per-meter)
A/m2: (amperes-per-square-meter)
A: (amperes)
Am2: (ampere-square-meters)
bars
BTU/h: (btus-per-hour)
BTU/lb dry: (btus-per-pound-dry-air)
BTU/lb: (btus-per-pound)
btus
cd/m2: (candelas-per-square-meter)
cd: (candelas)
cm H2O: (centimeters-of-water)
cm Hg: (centimeters-of-mercury)
cm: (centimeters)
cm2: (square-centimeters)
currency 1
currency 10
currency 2
currency 3
currency 4
currency 5
currency 6
currency 7
currency 8
currency 9
cycles-per-hour
cycles-per-minute
days
degrees-days-Celsius
degrees-days-Fahrenheit
deltaF: (delta-degrees-Fahrenheit)
deltaK: (delta-degrees-Kelvin)
F: (farads)
ft/min: (feet-per-minute)
ft/s: (feet-per-second)
ft: (feet)
ft2: (square-feet)
ft3/min: (cubic-feet-per-minute)
ft3/s: (cubic-feet-per-second)
ft3: (cubic-feet)
ftcd: (foot-candles)
g/m: (grams-per-minute)
g/s: (grams-per-second)
gal(uk)/min: (imperial-gallons-per-minute)
gal(uk): (imperial-gallons
gal/min: (us-gallons-per-minute)
gal: (us-gallons)
grams-of-water-per-kilogram-dry-air
H: (henrys)
hours
hp: (horsepower)
hPa: (hectopascals)
hundredths-seconds
Hz: (hertz)
in H2O: (inches-of-water)
in Hg: (inches-of-mercury)
in: (inches)
in2: (square-inches)
J/K: (joules-per-degree-Kelvin)
J/kg dry: (joules-per-kilogram-dry-air)
J/kgK: (joules-per-kilogram-degree-Kelvin)
J/s: (joule-seconds)
J: (joules)
kBTU/h: (kilo-btus-per-hour)
kBTU: (kilo-btus)
kg/h: (kilograms-per-hour)
kg/m: (kilograms-per-minute)
kg/m3: (kilograms-per-cubic-meter)
kg/s: (kilograms-per-second)
kg: (kilograms)
kHz: (kilohertz)
kilohms
kJ/K: (kilojoules-per-degree-Kelvin)
kJ/kg dry: (kilojoules-per-kilogram-dry-air)
kJ/kg: (kilojoules-per-kilogram)
kJ: (kilojoules)
km/hr: (kilometers-per-hour)
kPa: (kilopascals)
kV: (kilovolts)
kVA: (kilovolt-amperes)
kVAr: (kilovolt-amperes-reactive)
kW: (kilowatts)
kWh/m2: (kilowatt-hours-per-square-foot)
kWh/m2: (kilowatt-hours-per-square-meter)
kWh: (kilowatt-hours)
l/hr: (liters-per-hour)
l/min: (liters-per-minute)
l/s: (liters-per-second)
l: (liters)
lb/h: (pounds-mass-per-hour)
lb/m: (pounds-mass-per-minute)
lb/s: (pounds-mass-per-second)
lb: (pounds-mass)
lm: (lumens)
lx: (luxes)
m/hr: (meters-per-hour)
m/min: (meters-per-minute)
m/s/s: (meter-per-second-per-second)
m/s: (meters-per-second)
m: (meters)
m2/N: (square-meters-per-Newton)
m2: (square-meters)
m3/hr: (cubic-meters-per-hour)
m3/min: (cubic-meters-per-minute)
m3/s: (cubic-meters-per-second)
m3: (cubic-meters)
mA: (milliamperes)
mbar: (millibars)
MBTU: (mega-btus)
megohms
MHz: (megahertz)
milliohms
milliseconds
minutes
MJ/K: (megajoules-per-degree-Kelvin)
MJ/ft2: (megajoules-per-square-foot)
MJ/kg dry: (megajoules-per-kilogram-dry-air)
MJ/m2: (megajoules-per-square-meter)
MJ: (megajoules)
mm Hg: (millimeters-of-mercury)
mm/min: (millimeters-per-minute)
mm/s: (millimeters-per-second)
mm: (millimeters)
months
mph.: (miles-per-hour)
MV: (megavolts)
mV: (millivolts)
MVA: (megavolt-amperes)
MVAr: (megavolt-amperes-reactive)
MW: (megawatts)
mW: (milliwatts)
MWh: (megawatt-hours)
N/m: (newtons-per-meter)
N: (newton)
Nm: (newton-meters)
no-units
Ns: (newton-seconds)
ohm-meters
ohms
Pa: (pascals)
per: (percent)
percent-relative-humidity
per-minute
per-second
PF: (power-factor)
ppb: (parts-per-billion)
ppm: (parts-per-million)
psi/F: (psi-per-degree-Fahrenheit)
psi: (pounds-force-per-square-inch)
rad/s: (radians-per-second)
rad: (radians)
rpm: (revolutions-per-minute)
S/m: (siemens-per-meter)
S: (siemens)
seconds
t/h: (tons-per-hour)
T: (teslas)
t: (tons)
th: (ton-hours)
thm: (therms)
TR: (tons-refrigeration)
V/°K: (volts-per-degree-Kelvin)
V/m: (volts-per-meter)
V: (volts)
VA: (volt-amperes)
VAr: (volt-amperes-reactive)
W/ft2: (watts-per-square-foot)
W/m/K: (watts-per-meter-per-degree-Kelvin)
W/m2/K: (watts-per-square-meter-degree-kelvin)
W/m2: (watts-per-square-meter)
W: (watts)
Wb: (webers)
weeks
Wh: (watt-hours)
years