## Sheet1
Device Name: ge_sr750_760_rtu
Available Template Part number |  | Description
GE_SR750_760_RTU_T711 |  | Modbus RTU to BACnet MS/TP
GE_SR750_760_RTU_T147 |  | Modbus RTU to BACnet/IP
GE_SR750_760_RTU_T1275 |  | Modbus RTU to Allen-Bradley PLC
GE_SR750_760_RTU_T710 |  | Modbus TCP/IP to BACnet/IP
GE_SR750_760_RTU_T712 |  | Modbus TCP/IP to BACnet MS/TP
GE_SR750_760_RTU_T1276 |  | Modbus TCP/IP to Allen-Bradley PLC
Point | Point Name
1 | Neutral Voltage
2 | Sensitive Ground Current
3 | Phase A RMS Current
4 | Phase B RMS Current
5 | Phase C RMS Current
6 | Percent of Load-to-Trip
7 | Ground Current
8 | A-N RMS Voltage
9 | B-N RMS Voltage
10 | C-N RMS Voltage
11 | A-B RMS Voltage
12 | B-C RMS Voltage
13 | C-A RMS Voltage
14 | Average Current
15 | Average Line Voltage
16 | Average Phase Voltage
17 | Neutral Current
18 | 3Phase Real Power
19 | 3Phase Reactive Power
20 | 3Phase Apparent Power
21 | 3Phase Power Factor
22 | System Frequency
23 | Positive Watthours
24 | Last Phase A Current Demand
25 | Last Phase B Current Demand
26 | Last Phase C Current Demand
27 | Last Real Power Demand
28 | Last Reactive Power Demand
29 | Last Apparent Power Demand
30 | Max Phase A Current Demand
31 | Max Phase B Current Demand
32 | Max Phase C Current Demand
33 | Max Real Power Demand
34 | Max Reactive Power Demand
35 | Max Apparent Power Demand
36 | Phase A Real Power
37 | Phase A Reactive Power
38 | Phase A Apparent Power
39 | Phase A Power Factor
40 | Phase B Real Power
41 | Phase B Reactive Power
42 | Phase B Apparent Power
43 | Phase B Power Factor
44 | Phase C Real Power
45 | Phase C Reactive Power
46 | Phase C Apparent Power
47 | Phase C Power Factor

## Overall (hidden)
Read / Write
None
Read
Write
Read/Write

## Protocol_Selection (hidden)
Protocol 1 Selection | Protocol 2 Selection
Modbus RTU Master (MM) | BACnet/IP Server (BS)
Modbus TCP/IP Client (MC) | BACnet MS/TP Slave (BMS)

## Mapping (hidden)
Manipulation
None
Mult by 10.0
Mult by 100.0
Mult by 1000.0
Mult by 10000.0
Div by 10.0
Div by 100.0
Div by 1000.0
Div by 10000.0
Extract Bit 0
Extract Bit 1
Extract Bit 2
Extract Bit 3
Extract Bit 4
Extract Bit 5
Extract Bit 6
Extract Bit 7
Extract Bit 8
Extract Bit 9
Extract Bit 10
Extract Bit 11
Extract Bit 12
Extract Bit 13
Extract Bit 14
Extract Bit 15
Extract Bit 16
Extract Bit 17
Extract Bit 18
Extract Bit 19
Extract Bit 20
Extract Bit 21
Extract Bit 22
Extract Bit 23
Extract Bit 24
Extract Bit 25
Extract Bit 26
Extract Bit 27
Extract Bit 28
Extract Bit 29
Extract Bit 30
Extract Bit 31
Extract Bit 32
Extract Bit 33
Extract Bit 34
Extract Bit 35
Extract Bit 36
Extract Bit 37
Extract Bit 38
Extract Bit 39
Extract Bit 40
Extract Bit 41
Extract Bit 42
Extract Bit 43
Extract Bit 44
Extract Bit 45
Extract Bit 46
Extract Bit 47
Extract Bit 48
Extract Bit 49
Extract Bit 50
Extract Bit 51
Extract Bit 52
Extract Bit 53
Extract Bit 54
Extract Bit 55
Extract Bit 56
Extract Bit 57
Extract Bit 58
Extract Bit 59
Extract Bit 60
Extract Bit 61
Extract Bit 62
Extract Bit 63

## Modbus_Configuration (hidden)
Modbus Data Types | Modbus Read Data Types | Modbus Write Data Types | Max Address per Request by Data Type
0x Coil Status (Bit) | 0x Coil Status (Bit) | 0x Coil Status (Bit) | 512
1x Input Status (Bit) | 1x Input Status (Bit) | 4x Holding Register (16 Bit Int) | 125
3x Input Register (16 Bit Int) | 3x Input Register (16 Bit Int) | 4x Holding Register (16 Bit Uint) | 125
3x Input Register (16 Bit Uint) | 3x Input Register (16 Bit Uint) | 4x Holding Register (32 Bit Int) | 62
3x Input Register (32 Bit Int) | 3x Input Register (32 Bit Int) | 4x Holding Register (32 Bit Uint) | 31
3x Input Register (32 Bit Uint) | 3x Input Register (32 Bit Uint) | 4x Holding Register (32 Bit Float)
3x Input Register (32 Bit Float) | 3x Input Register (32 Bit Float) | 4x Holding Register (64 Bit Int)
3x Input Register (64 Bit Int) | 3x Input Register (64 Bit Int) | 4x Holding Register (64 Bit Uint)
3x Input Register (64 Bit Uint) | 3x Input Register (64 Bit Uint) | 4x Holding Register (64 Bit Float)
3x Input Register (64 Bit Float) | 3x Input Register (64 Bit Float)
4x Holding Register (16 Bit Int) | 4x Holding Register (16 Bit Int)
4x Holding Register (16 Bit Uint) | 4x Holding Register (16 Bit Uint)
4x Holding Register (32 Bit Int) | 4x Holding Register (32 Bit Int)
4x Holding Register (32 Bit Uint) | 4x Holding Register (32 Bit Uint)
4x Holding Register (32 Bit Float) | 4x Holding Register (32 Bit Float)
4x Holding Register (64 Bit Int) | 4x Holding Register (64 Bit Int)
4x Holding Register (64 Bit Uint) | 4x Holding Register (64 Bit Uint)
4x Holding Register (64 Bit Float) | 4x Holding Register (64 Bit Float)

## BACnet_Configuration (hidden)
BACnet Object Types | BACnet Read Object Types | BACnet Write Object Types | BACnet Units
Analog Input | Analog Input | Analog Output | %/s: (percent-per-second)
Analog Output | Binary Input | Binary Output | %obs/ft: (percent-obscuration-per-foot)
Binary Input | Character String Value | Character String Value | %obs/m: (percent-obscuration-per-meter)
Binary Output |  |  | /h: (per-hour)
Character String Value |  |  | ang: (degrees-angular)
C/h: (degrees-Celsius-per-hour)
C/m: (degrees-Celsius-per-minute)
C: (degrees-Celsius)
F/h: (degrees-Fahrenheit-per-hour)
F/m: (degrees-Fahrenheit-per-minute)
F: (degrees-Fahrenheit)
K/h: (degrees-Kelvin-per-hour)
K/m: (degrees-Kelvin-per-minute)
K: (degrees-Kelvin)
phase: (degrees-phase)
A/m: (amperes-per-meter)
A/m2: (amperes-per-square-meter)
A: (amperes)
Am2: (ampere-square-meters)
bars
BTU/h: (btus-per-hour)
BTU/lb dry: (btus-per-pound-dry-air)
BTU/lb: (btus-per-pound)
btus
cd/m2: (candelas-per-square-meter)
cd: (candelas)
cm H2O: (centimeters-of-water)
cm Hg: (centimeters-of-mercury)
cm: (centimeters)
cm2: (square-centimeters)
currency 1
currency 10
currency 2
currency 3
currency 4
currency 5
currency 6
currency 7
currency 8
currency 9
cycles-per-hour
cycles-per-minute
days
degrees-days-Celsius
degrees-days-Fahrenheit
deltaF: (delta-degrees-Fahrenheit)
deltaK: (delta-degrees-Kelvin)
F: (farads)
ft/min: (feet-per-minute)
ft/s: (feet-per-second)
ft: (feet)
ft2: (square-feet)
ft3/min: (cubic-feet-per-minute)
ft3/s: (cubic-feet-per-second)
ft3: (cubic-feet)
ftcd: (foot-candles)
g/m: (grams-per-minute)
g/s: (grams-per-second)
gal(uk)/min: (imperial-gallons-per-minute)
gal(uk): (imperial-gallons
gal/min: (us-gallons-per-minute)
gal: (us-gallons)
grams-of-water-per-kilogram-dry-air
H: (henrys)
hours
hp: (horsepower)
hPa: (hectopascals)
hundredths-seconds
Hz: (hertz)
in H2O: (inches-of-water)
in Hg: (inches-of-mercury)
in: (inches)
in2: (square-inches)
J/K: (joules-per-degree-Kelvin)
J/kg dry: (joules-per-kilogram-dry-air)
J/kgK: (joules-per-kilogram-degree-Kelvin)
J/s: (joule-seconds)
J: (joules)
kBTU/h: (kilo-btus-per-hour)
kBTU: (kilo-btus)
kg/h: (kilograms-per-hour)
kg/m: (kilograms-per-minute)
kg/m3: (kilograms-per-cubic-meter)
kg/s: (kilograms-per-second)
kg: (kilograms)
kHz: (kilohertz)
kilohms
kJ/K: (kilojoules-per-degree-Kelvin)
kJ/kg dry: (kilojoules-per-kilogram-dry-air)
kJ/kg: (kilojoules-per-kilogram)
kJ: (kilojoules)
km/hr: (kilometers-per-hour)
kPa: (kilopascals)
kV: (kilovolts)
kVA: (kilovolt-amperes)
kVAr: (kilovolt-amperes-reactive)
kW: (kilowatts)
kWh/m2: (kilowatt-hours-per-square-foot)
kWh/m2: (kilowatt-hours-per-square-meter)
kWh: (kilowatt-hours)
l/hr: (liters-per-hour)
l/min: (liters-per-minute)
l/s: (liters-per-second)
l: (liters)
lb/h: (pounds-mass-per-hour)
lb/m: (pounds-mass-per-minute)
lb/s: (pounds-mass-per-second)
lb: (pounds-mass)
lm: (lumens)
lx: (luxes)
m/hr: (meters-per-hour)
m/min: (meters-per-minute)
m/s/s: (meter-per-second-per-second)
m/s: (meters-per-second)
m: (meters)
m2/N: (square-meters-per-Newton)
m2: (square-meters)
m3/hr: (cubic-meters-per-hour)
m3/min: (cubic-meters-per-minute)
m3/s: (cubic-meters-per-second)
m3: (cubic-meters)
mA: (milliamperes)
mbar: (millibars)
MBTU: (mega-btus)
megohms
MHz: (megahertz)
milliohms
milliseconds
minutes
MJ/K: (megajoules-per-degree-Kelvin)
MJ/ft2: (megajoules-per-square-foot)
MJ/kg dry: (megajoules-per-kilogram-dry-air)
MJ/m2: (megajoules-per-square-meter)
MJ: (megajoules)
mm Hg: (millimeters-of-mercury)
mm/min: (millimeters-per-minute)
mm/s: (millimeters-per-second)
mm: (millimeters)
months
mph.: (miles-per-hour)
MV: (megavolts)
mV: (millivolts)
MVA: (megavolt-amperes)
MVAr: (megavolt-amperes-reactive)
MW: (megawatts)
mW: (milliwatts)
MWh: (megawatt-hours)
N/m: (newtons-per-meter)
N: (newton)
Nm: (newton-meters)
no-units
Ns: (newton-seconds)
ohm-meters
ohms
Pa: (pascals)
per: (percent)
percent-relative-humidity
per-minute
per-second
PF: (power-factor)
ppb: (parts-per-billion)
ppm: (parts-per-million)
psi/F: (psi-per-degree-Fahrenheit)
psi: (pounds-force-per-square-inch)
rad/s: (radians-per-second)
rad: (radians)
rpm: (revolutions-per-minute)
S/m: (siemens-per-meter)
S: (siemens)
seconds
t/h: (tons-per-hour)
T: (teslas)
t: (tons)
th: (ton-hours)
thm: (therms)
TR: (tons-refrigeration)
V/°K: (volts-per-degree-Kelvin)
V/m: (volts-per-meter)
V: (volts)
VA: (volt-amperes)
VAr: (volt-amperes-reactive)
W/ft2: (watts-per-square-foot)
W/m/K: (watts-per-meter-per-degree-Kelvin)
W/m2/K: (watts-per-square-meter-degree-kelvin)
W/m2: (watts-per-square-meter)
W: (watts)
Wb: (webers)
weeks
Wh: (watt-hours)
years