## Sheet1
Device Name: kam_dpm
Available Template Part number |  | Description
KAM_DPM_T739 |  | Modbus RTU to BACnet MS/TP
KAM_DPM_T163 |  | Modbus RTU to BACnet/IP
KAM_DPM_T1295 |  | Modbus RTU to Allen-Bradley PLC
KAM_DPM_T738 |  | Modbus TCP/IP to BACnet/IP
KAM_DPM_T740 |  | Modbus TCP/IP to BACnet MS/TP
KAM_DPM_T1296 |  | Modbus TCP/IP to Allen-Bradley PLC
Point | Point Name
1 | Phase 1 Current
2 | Phase 2 Current
3 | Phase 3 Current
4 | Neutral Current
5 | Phase to Phase Voltage U12
6 | Phase to Phase Voltage U23
7 | Phase to Phase Voltage U31
8 | Phase to Neutral voltage Phase 1
9 | Phase to Neutral voltage Phase 2
10 | Phase to Neutral voltage Phase 3
11 | Frequency
12 | Sum Active Power +/-
13 | Sum Reactive Power +/-
14 | Sum Apparent Power +/-
15 | Sum Power Factor +/-
16 | Active Power Phase 1 +/-
17 | Active Power Phase 2 +/-
18 | Active Power Phase 3 +/-
19 | Reactive Power Phase 1 +/-
20 | Reactive Power Phase 2 +/-
21 | Reactive Power Phase 3 +/-
22 | Apparent Power Phase 1
23 | Apparent Power Phase 2
24 | Apparent Power Phase 3
25 | Power Factor Phase 1
26 | Power Factor Phase 2
27 | Power Factor Phase 3
28 | Average Value I1
29 | Average Value I2
30 | Average Value I3
31 | Avg Value Sum Active Power +
32 | Avg Value Sum Active Power -
33 | Avg Value Sum Reactive Power +
34 | Avg Value Sum Reactive Power -
35 | Avg Value Sum Apparent Power
36 | Maximum Value I1
37 | Maximum Value I2
38 | Maximum Value I3
39 | Max Value Sum Active Power +
40 | Max Value Sum Active Power -
41 | Max Value Sum Reactive Power +
42 | Max Value Sum Reactive Power -
43 | Max Value Sum Apparent Power
44 | Active Energy +
45 | Reactive Energy +
46 | Apparent Energy
47 | Active Energy -
48 | Reactive Energy-

## Overall (hidden)
Read / Write
None
Read
Write
Read/Write

## Protocol_Selection (hidden)
Protocol 1 Selection | Protocol 2 Selection
Modbus RTU Master (MM) | BACnet/IP Server (BS)
Modbus TCP/IP Client (MC) | BACnet MS/TP Slave (BMS)

## Mapping (hidden)
Manipulation
None
Mult by 10.0
Mult by 100.0
Mult by 1000.0
Mult by 10000.0
Div by 10.0
Div by 100.0
Div by 1000.0
Div by 10000.0
Extract Bit 0
Extract Bit 1
Extract Bit 2
Extract Bit 3
Extract Bit 4
Extract Bit 5
Extract Bit 6
Extract Bit 7
Extract Bit 8
Extract Bit 9
Extract Bit 10
Extract Bit 11
Extract Bit 12
Extract Bit 13
Extract Bit 14
Extract Bit 15
Extract Bit 16
Extract Bit 17
Extract Bit 18
Extract Bit 19
Extract Bit 20
Extract Bit 21
Extract Bit 22
Extract Bit 23
Extract Bit 24
Extract Bit 25
Extract Bit 26
Extract Bit 27
Extract Bit 28
Extract Bit 29
Extract Bit 30
Extract Bit 31
Extract Bit 32
Extract Bit 33
Extract Bit 34
Extract Bit 35
Extract Bit 36
Extract Bit 37
Extract Bit 38
Extract Bit 39
Extract Bit 40
Extract Bit 41
Extract Bit 42
Extract Bit 43
Extract Bit 44
Extract Bit 45
Extract Bit 46
Extract Bit 47
Extract Bit 48
Extract Bit 49
Extract Bit 50
Extract Bit 51
Extract Bit 52
Extract Bit 53
Extract Bit 54
Extract Bit 55
Extract Bit 56
Extract Bit 57
Extract Bit 58
Extract Bit 59
Extract Bit 60
Extract Bit 61
Extract Bit 62
Extract Bit 63

## Modbus_Configuration (hidden)
Modbus Data Types | Modbus Read Data Types | Modbus Write Data Types | Max Address per Request by Data Type
0x Coil Status (Bit) | 0x Coil Status (Bit) | 0x Coil Status (Bit) | 512
1x Input Status (Bit) | 1x Input Status (Bit) | 4x Holding Register (16 Bit Int) | 125
3x Input Register (16 Bit Int) | 3x Input Register (16 Bit Int) | 4x Holding Register (16 Bit Uint) | 125
3x Input Register (16 Bit Uint) | 3x Input Register (16 Bit Uint) | 4x Holding Register (32 Bit Int) | 62
3x Input Register (32 Bit Int) | 3x Input Register (32 Bit Int) | 4x Holding Register (32 Bit Uint) | 31
3x Input Register (32 Bit Uint) | 3x Input Register (32 Bit Uint) | 4x Holding Register (32 Bit Float)
3x Input Register (32 Bit Float) | 3x Input Register (32 Bit Float) | 4x Holding Register (64 Bit Int)
3x Input Register (64 Bit Int) | 3x Input Register (64 Bit Int) | 4x Holding Register (64 Bit Uint)
3x Input Register (64 Bit Uint) | 3x Input Register (64 Bit Uint) | 4x Holding Register (64 Bit Float)
3x Input Register (64 Bit Float) | 3x Input Register (64 Bit Float)
4x Holding Register (16 Bit Int) | 4x Holding Register (16 Bit Int)
4x Holding Register (16 Bit Uint) | 4x Holding Register (16 Bit Uint)
4x Holding Register (32 Bit Int) | 4x Holding Register (32 Bit Int)
4x Holding Register (32 Bit Uint) | 4x Holding Register (32 Bit Uint)
4x Holding Register (32 Bit Float) | 4x Holding Register (32 Bit Float)
4x Holding Register (64 Bit Int) | 4x Holding Register (64 Bit Int)
4x Holding Register (64 Bit Uint) | 4x Holding Register (64 Bit Uint)
4x Holding Register (64 Bit Float) | 4x Holding Register (64 Bit Float)

## BACnet_Configuration (hidden)
BACnet Object Types | BACnet Read Object Types | BACnet Write Object Types | BACnet Units
Analog Input | Analog Input | Analog Output | %/s: (percent-per-second)
Analog Output | Binary Input | Binary Output | %obs/ft: (percent-obscuration-per-foot)
Binary Input | Character String Value | Character String Value | %obs/m: (percent-obscuration-per-meter)
Binary Output |  |  | /h: (per-hour)
Character String Value |  |  | ang: (degrees-angular)
C/h: (degrees-Celsius-per-hour)
C/m: (degrees-Celsius-per-minute)
C: (degrees-Celsius)
F/h: (degrees-Fahrenheit-per-hour)
F/m: (degrees-Fahrenheit-per-minute)
F: (degrees-Fahrenheit)
K/h: (degrees-Kelvin-per-hour)
K/m: (degrees-Kelvin-per-minute)
K: (degrees-Kelvin)
phase: (degrees-phase)
A/m: (amperes-per-meter)
A/m2: (amperes-per-square-meter)
A: (amperes)
Am2: (ampere-square-meters)
bars
BTU/h: (btus-per-hour)
BTU/lb dry: (btus-per-pound-dry-air)
BTU/lb: (btus-per-pound)
btus
cd/m2: (candelas-per-square-meter)
cd: (candelas)
cm H2O: (centimeters-of-water)
cm Hg: (centimeters-of-mercury)
cm: (centimeters)
cm2: (square-centimeters)
currency 1
currency 10
currency 2
currency 3
currency 4
currency 5
currency 6
currency 7
currency 8
currency 9
cycles-per-hour
cycles-per-minute
days
degrees-days-Celsius
degrees-days-Fahrenheit
deltaF: (delta-degrees-Fahrenheit)
deltaK: (delta-degrees-Kelvin)
F: (farads)
ft/min: (feet-per-minute)
ft/s: (feet-per-second)
ft: (feet)
ft2: (square-feet)
ft3/min: (cubic-feet-per-minute)
ft3/s: (cubic-feet-per-second)
ft3: (cubic-feet)
ftcd: (foot-candles)
g/m: (grams-per-minute)
g/s: (grams-per-second)
gal(uk)/min: (imperial-gallons-per-minute)
gal(uk): (imperial-gallons
gal/min: (us-gallons-per-minute)
gal: (us-gallons)
grams-of-water-per-kilogram-dry-air
H: (henrys)
hours
hp: (horsepower)
hPa: (hectopascals)
hundredths-seconds
Hz: (hertz)
in H2O: (inches-of-water)
in Hg: (inches-of-mercury)
in: (inches)
in2: (square-inches)
J/K: (joules-per-degree-Kelvin)
J/kg dry: (joules-per-kilogram-dry-air)
J/kgK: (joules-per-kilogram-degree-Kelvin)
J/s: (joule-seconds)
J: (joules)
kBTU/h: (kilo-btus-per-hour)
kBTU: (kilo-btus)
kg/h: (kilograms-per-hour)
kg/m: (kilograms-per-minute)
kg/m3: (kilograms-per-cubic-meter)
kg/s: (kilograms-per-second)
kg: (kilograms)
kHz: (kilohertz)
kilohms
kJ/K: (kilojoules-per-degree-Kelvin)
kJ/kg dry: (kilojoules-per-kilogram-dry-air)
kJ/kg: (kilojoules-per-kilogram)
kJ: (kilojoules)
km/hr: (kilometers-per-hour)
kPa: (kilopascals)
kV: (kilovolts)
kVA: (kilovolt-amperes)
kVAr: (kilovolt-amperes-reactive)
kW: (kilowatts)
kWh/m2: (kilowatt-hours-per-square-foot)
kWh/m2: (kilowatt-hours-per-square-meter)
kWh: (kilowatt-hours)
l/hr: (liters-per-hour)
l/min: (liters-per-minute)
l/s: (liters-per-second)
l: (liters)
lb/h: (pounds-mass-per-hour)
lb/m: (pounds-mass-per-minute)
lb/s: (pounds-mass-per-second)
lb: (pounds-mass)
lm: (lumens)
lx: (luxes)
m/hr: (meters-per-hour)
m/min: (meters-per-minute)
m/s/s: (meter-per-second-per-second)
m/s: (meters-per-second)
m: (meters)
m2/N: (square-meters-per-Newton)
m2: (square-meters)
m3/hr: (cubic-meters-per-hour)
m3/min: (cubic-meters-per-minute)
m3/s: (cubic-meters-per-second)
m3: (cubic-meters)
mA: (milliamperes)
mbar: (millibars)
MBTU: (mega-btus)
megohms
MHz: (megahertz)
milliohms
milliseconds
minutes
MJ/K: (megajoules-per-degree-Kelvin)
MJ/ft2: (megajoules-per-square-foot)
MJ/kg dry: (megajoules-per-kilogram-dry-air)
MJ/m2: (megajoules-per-square-meter)
MJ: (megajoules)
mm Hg: (millimeters-of-mercury)
mm/min: (millimeters-per-minute)
mm/s: (millimeters-per-second)
mm: (millimeters)
months
mph.: (miles-per-hour)
MV: (megavolts)
mV: (millivolts)
MVA: (megavolt-amperes)
MVAr: (megavolt-amperes-reactive)
MW: (megawatts)
mW: (milliwatts)
MWh: (megawatt-hours)
N/m: (newtons-per-meter)
N: (newton)
Nm: (newton-meters)
no-units
Ns: (newton-seconds)
ohm-meters
ohms
Pa: (pascals)
per: (percent)
percent-relative-humidity
per-minute
per-second
PF: (power-factor)
ppb: (parts-per-billion)
ppm: (parts-per-million)
psi/F: (psi-per-degree-Fahrenheit)
psi: (pounds-force-per-square-inch)
rad/s: (radians-per-second)
rad: (radians)
rpm: (revolutions-per-minute)
S/m: (siemens-per-meter)
S: (siemens)
seconds
t/h: (tons-per-hour)
T: (teslas)
t: (tons)
th: (ton-hours)
thm: (therms)
TR: (tons-refrigeration)
V/°K: (volts-per-degree-Kelvin)
V/m: (volts-per-meter)
V: (volts)
VA: (volt-amperes)
VAr: (volt-amperes-reactive)
W/ft2: (watts-per-square-foot)
W/m/K: (watts-per-meter-per-degree-Kelvin)
W/m2/K: (watts-per-square-meter-degree-kelvin)
W/m2: (watts-per-square-meter)
W: (watts)
Wb: (webers)
weeks
Wh: (watt-hours)
years