## Sheet1
Device Name: kohler_decisionmaker3000
Available Template Part number |  | Description
Kohler_DecisionMaker3000_T757 |  | Modbus RTU to BACnet MS/TP
Kohler_DecisionMaker3000_T318 |  | Modbus RTU to BACnet/IP
Kohler_DecisionMaker3000_T1313 |  | Modbus RTU to Allen-Bradley PLC
Kohler_DecisionMaker3000_T179 |  | Modbus TCP/IP to BACnet/IP
Kohler_DecisionMaker3000_T178 |  | Modbus TCP/IP to BACnet MS/TP
Kohler_DecisionMaker3000_T1314 |  | Modbus TCP/IP to Allen-Bradley PLC
Point | Point Name
1 | EngineSpeed
2 | EngineOilPressure
3 | EngineCoolantTemperature
4 | BatteryVoltage
5 | EngineLowOilPressureSwitch
6 | EngineHighCoolTemperatureSwitch
7 | EngineLowCoolTemperatureSwitch
8 | EngineLowFuelLevelSwitch
9 | GeneratorTruePowerA
10 | GeneratorTruePowerB
11 | GeneratorTruePowerC
12 | GeneratorTrueTotalPower
13 | GeneratorVoltageAB
14 | GeneratorVoltageBC
15 | GeneratorVoltageCA
16 | GeneratorVoltageAveLineToLine
17 | GeneratorVoltageAN
18 | GeneratorVoltageBN
19 | GeneratorVoltageCN
20 | GeneratorVoltageAveLineToNeutral
21 | GeneratorCurrentA
22 | GeneratorCurrentB
23 | GeneratorCurrentC
24 | GeneratorCurrentAverage
25 | GeneratorFrequency
26 | EngineTotalRunTime
27 | EngineTotalRunTimeLoaded
28 | DeviceEvent ID
29 | DeviceEvent Level
30 | DeviceEvent Fmi
31 | DeviceEvent Parameter ID

## Overall (hidden)
Read / Write
None
Read
Write
Read/Write

## Protocol_Selection (hidden)
Protocol 1 Selection | Protocol 2 Selection
Modbus RTU Master (MM) | BACnet/IP Server (BS)
Modbus TCP/IP Client (MC) | BACnet MS/TP Slave (BMS)

## Mapping (hidden)
Manipulation
None
Mult by 10.0
Mult by 100.0
Mult by 1000.0
Mult by 10000.0
Div by 10.0
Div by 100.0
Div by 1000.0
Div by 10000.0
Extract Bit 0
Extract Bit 1
Extract Bit 2
Extract Bit 3
Extract Bit 4
Extract Bit 5
Extract Bit 6
Extract Bit 7
Extract Bit 8
Extract Bit 9
Extract Bit 10
Extract Bit 11
Extract Bit 12
Extract Bit 13
Extract Bit 14
Extract Bit 15
Extract Bit 16
Extract Bit 17
Extract Bit 18
Extract Bit 19
Extract Bit 20
Extract Bit 21
Extract Bit 22
Extract Bit 23
Extract Bit 24
Extract Bit 25
Extract Bit 26
Extract Bit 27
Extract Bit 28
Extract Bit 29
Extract Bit 30
Extract Bit 31
Extract Bit 32
Extract Bit 33
Extract Bit 34
Extract Bit 35
Extract Bit 36
Extract Bit 37
Extract Bit 38
Extract Bit 39
Extract Bit 40
Extract Bit 41
Extract Bit 42
Extract Bit 43
Extract Bit 44
Extract Bit 45
Extract Bit 46
Extract Bit 47
Extract Bit 48
Extract Bit 49
Extract Bit 50
Extract Bit 51
Extract Bit 52
Extract Bit 53
Extract Bit 54
Extract Bit 55
Extract Bit 56
Extract Bit 57
Extract Bit 58
Extract Bit 59
Extract Bit 60
Extract Bit 61
Extract Bit 62
Extract Bit 63

## Modbus_Configuration (hidden)
Modbus Data Types | Modbus Read Data Types | Modbus Write Data Types | Max Address per Request by Data Type
0x Coil Status (Bit) | 0x Coil Status (Bit) | 0x Coil Status (Bit) | 512
1x Input Status (Bit) | 1x Input Status (Bit) | 4x Holding Register (16 Bit Int) | 125
3x Input Register (16 Bit Int) | 3x Input Register (16 Bit Int) | 4x Holding Register (16 Bit Uint) | 125
3x Input Register (16 Bit Uint) | 3x Input Register (16 Bit Uint) | 4x Holding Register (32 Bit Int) | 62
3x Input Register (32 Bit Int) | 3x Input Register (32 Bit Int) | 4x Holding Register (32 Bit Uint) | 31
3x Input Register (32 Bit Uint) | 3x Input Register (32 Bit Uint) | 4x Holding Register (32 Bit Float)
3x Input Register (32 Bit Float) | 3x Input Register (32 Bit Float) | 4x Holding Register (64 Bit Int)
3x Input Register (64 Bit Int) | 3x Input Register (64 Bit Int) | 4x Holding Register (64 Bit Uint)
3x Input Register (64 Bit Uint) | 3x Input Register (64 Bit Uint) | 4x Holding Register (64 Bit Float)
3x Input Register (64 Bit Float) | 3x Input Register (64 Bit Float)
4x Holding Register (16 Bit Int) | 4x Holding Register (16 Bit Int)
4x Holding Register (16 Bit Uint) | 4x Holding Register (16 Bit Uint)
4x Holding Register (32 Bit Int) | 4x Holding Register (32 Bit Int)
4x Holding Register (32 Bit Uint) | 4x Holding Register (32 Bit Uint)
4x Holding Register (32 Bit Float) | 4x Holding Register (32 Bit Float)
4x Holding Register (64 Bit Int) | 4x Holding Register (64 Bit Int)
4x Holding Register (64 Bit Uint) | 4x Holding Register (64 Bit Uint)
4x Holding Register (64 Bit Float) | 4x Holding Register (64 Bit Float)

## BACnet_Configuration (hidden)
BACnet Object Types | BACnet Read Object Types | BACnet Write Object Types | BACnet Units
Analog Input | Analog Input | Analog Output | %/s: (percent-per-second)
Analog Output | Binary Input | Binary Output | %obs/ft: (percent-obscuration-per-foot)
Binary Input | Character String Value | Character String Value | %obs/m: (percent-obscuration-per-meter)
Binary Output |  |  | /h: (per-hour)
Character String Value |  |  | ang: (degrees-angular)
C/h: (degrees-Celsius-per-hour)
C/m: (degrees-Celsius-per-minute)
C: (degrees-Celsius)
F/h: (degrees-Fahrenheit-per-hour)
F/m: (degrees-Fahrenheit-per-minute)
F: (degrees-Fahrenheit)
K/h: (degrees-Kelvin-per-hour)
K/m: (degrees-Kelvin-per-minute)
K: (degrees-Kelvin)
phase: (degrees-phase)
A/m: (amperes-per-meter)
A/m2: (amperes-per-square-meter)
A: (amperes)
Am2: (ampere-square-meters)
bars
BTU/h: (btus-per-hour)
BTU/lb dry: (btus-per-pound-dry-air)
BTU/lb: (btus-per-pound)
btus
cd/m2: (candelas-per-square-meter)
cd: (candelas)
cm H2O: (centimeters-of-water)
cm Hg: (centimeters-of-mercury)
cm: (centimeters)
cm2: (square-centimeters)
currency 1
currency 10
currency 2
currency 3
currency 4
currency 5
currency 6
currency 7
currency 8
currency 9
cycles-per-hour
cycles-per-minute
days
degrees-days-Celsius
degrees-days-Fahrenheit
deltaF: (delta-degrees-Fahrenheit)
deltaK: (delta-degrees-Kelvin)
F: (farads)
ft/min: (feet-per-minute)
ft/s: (feet-per-second)
ft: (feet)
ft2: (square-feet)
ft3/min: (cubic-feet-per-minute)
ft3/s: (cubic-feet-per-second)
ft3: (cubic-feet)
ftcd: (foot-candles)
g/m: (grams-per-minute)
g/s: (grams-per-second)
gal(uk)/min: (imperial-gallons-per-minute)
gal(uk): (imperial-gallons
gal/min: (us-gallons-per-minute)
gal: (us-gallons)
grams-of-water-per-kilogram-dry-air
H: (henrys)
hours
hp: (horsepower)
hPa: (hectopascals)
hundredths-seconds
Hz: (hertz)
in H2O: (inches-of-water)
in Hg: (inches-of-mercury)
in: (inches)
in2: (square-inches)
J/K: (joules-per-degree-Kelvin)
J/kg dry: (joules-per-kilogram-dry-air)
J/kgK: (joules-per-kilogram-degree-Kelvin)
J/s: (joule-seconds)
J: (joules)
kBTU/h: (kilo-btus-per-hour)
kBTU: (kilo-btus)
kg/h: (kilograms-per-hour)
kg/m: (kilograms-per-minute)
kg/m3: (kilograms-per-cubic-meter)
kg/s: (kilograms-per-second)
kg: (kilograms)
kHz: (kilohertz)
kilohms
kJ/K: (kilojoules-per-degree-Kelvin)
kJ/kg dry: (kilojoules-per-kilogram-dry-air)
kJ/kg: (kilojoules-per-kilogram)
kJ: (kilojoules)
km/hr: (kilometers-per-hour)
kPa: (kilopascals)
kV: (kilovolts)
kVA: (kilovolt-amperes)
kVAr: (kilovolt-amperes-reactive)
kW: (kilowatts)
kWh/m2: (kilowatt-hours-per-square-foot)
kWh/m2: (kilowatt-hours-per-square-meter)
kWh: (kilowatt-hours)
l/hr: (liters-per-hour)
l/min: (liters-per-minute)
l/s: (liters-per-second)
l: (liters)
lb/h: (pounds-mass-per-hour)
lb/m: (pounds-mass-per-minute)
lb/s: (pounds-mass-per-second)
lb: (pounds-mass)
lm: (lumens)
lx: (luxes)
m/hr: (meters-per-hour)
m/min: (meters-per-minute)
m/s/s: (meter-per-second-per-second)
m/s: (meters-per-second)
m: (meters)
m2/N: (square-meters-per-Newton)
m2: (square-meters)
m3/hr: (cubic-meters-per-hour)
m3/min: (cubic-meters-per-minute)
m3/s: (cubic-meters-per-second)
m3: (cubic-meters)
mA: (milliamperes)
mbar: (millibars)
MBTU: (mega-btus)
megohms
MHz: (megahertz)
milliohms
milliseconds
minutes
MJ/K: (megajoules-per-degree-Kelvin)
MJ/ft2: (megajoules-per-square-foot)
MJ/kg dry: (megajoules-per-kilogram-dry-air)
MJ/m2: (megajoules-per-square-meter)
MJ: (megajoules)
mm Hg: (millimeters-of-mercury)
mm/min: (millimeters-per-minute)
mm/s: (millimeters-per-second)
mm: (millimeters)
months
mph.: (miles-per-hour)
MV: (megavolts)
mV: (millivolts)
MVA: (megavolt-amperes)
MVAr: (megavolt-amperes-reactive)
MW: (megawatts)
mW: (milliwatts)
MWh: (megawatt-hours)
N/m: (newtons-per-meter)
N: (newton)
Nm: (newton-meters)
no-units
Ns: (newton-seconds)
ohm-meters
ohms
Pa: (pascals)
per: (percent)
percent-relative-humidity
per-minute
per-second
PF: (power-factor)
ppb: (parts-per-billion)
ppm: (parts-per-million)
psi/F: (psi-per-degree-Fahrenheit)
psi: (pounds-force-per-square-inch)
rad/s: (radians-per-second)
rad: (radians)
rpm: (revolutions-per-minute)
S/m: (siemens-per-meter)
S: (siemens)
seconds
t/h: (tons-per-hour)
T: (teslas)
t: (tons)
th: (ton-hours)
thm: (therms)
TR: (tons-refrigeration)
V/°K: (volts-per-degree-Kelvin)
V/m: (volts-per-meter)
V: (volts)
VA: (volt-amperes)
VAr: (volt-amperes-reactive)
W/ft2: (watts-per-square-foot)
W/m/K: (watts-per-meter-per-degree-Kelvin)
W/m2/K: (watts-per-square-meter-degree-kelvin)
W/m2: (watts-per-square-meter)
W: (watts)
Wb: (webers)
weeks
Wh: (watt-hours)
years