## Sheet1
Device Name: ABB_ACS310
Available Template Part number |  | Description
Red Lion DSP_T283 |  | Modbus RTU to BACnet MS/TP
Red Lion DSP_T816 |  | Modbus RTU to BACnet/IP
Red Lion DSP_T1355 |  | Modbus RTU to Allen-Bradley PLC
Red Lion DSP_T817 |  | Modbus TCP/IP to BACnet/IP
Red Lion DSP_T818 |  | Modbus TCP/IP to BACnet MS/TP
Red Lion DSP_T1356 |  | Modbus TCP/IP to Allen-Bradley PLC
Point | Point Name
1 | LOW_COOLANT_LVL
2 | SWITCHGEAR_ESTOP
3 | HIGH_COOLANT_TEMP
4 | LOW_OIL_PRES
5 | OVER_CRANK
6 | OVER_SPEED
7 | UNDER_FREQ
8 | OVER_FREQ
9 | UNDER_VOLTAGE
10 | OVER_VOLTAGE
11 | REV_PWR
12 | LOF
13 | CB_TRIPPED
14 | GND_FLT
15 | CRITICAL_LOW_FUEL
16 | HIGH_WINDING_TEMP
17 | OVEREXCITATION
18 | MOUNTED_CB_TRIPPED
19 | MFR_FAILURE
20 | EMCP_ESTOP
21 | HIGH_COOLANT_TEMP
22 | LOW_COOLANT_TEMP
23 | LOW_OIL_PRESS
24 | LOW_BATT_VOLT
25 | HI_BATT_VOLT
26 | BATT_CHG_FAILURE
27 | CB_FTC
28 | CB_FTO
29 | EMCP_COMM_ALM
30 | XDCR_FAULT
31 | FTS
32 | LOW_FUEL
33 | SYNC_NIA
34 | EMCP_NIA
35 | GEN_ECS_NIA
36 | PREALARM_16
37 | GND_FAULT
38 | RUTURE_BASIN
39 | HIGH_FUEL
40 | MFR_FAILURE
41 | HI_WINDING_TEMP
42 | HI_BEARING_TEMP
43 | CB_NOT_CONNECT
44 | CBCS_IN_PTL
45 | GenFault
46 | Genaux
47 | GenPre_alarm
48 | GEN_ALARM_ACTIVE
49 | GenPLCOK
50 | GenECS_Off
51 | GenHorn
52 | GenokToClose
53 | CoolDown
54 | Gen_PB_ACK
55 | GenTripped
56 | Gen_NIA
57 | Gen_CB_open_status
58 | Running
59 | Gen_Transducer_Fault
60 | GenNotAvail
61 | HMI_GEN_PB_ACK
62 | GenECS_Off
63 | GenECS_Auto
64 | GenECS_Man
65 | GenECS_CDS
66 | Sync_Switch_Off
67 | Sync_Switch_Auto
68 | Sync_Switch_Manual
69 | Sync_Switch_Check
70 | HMI_GEN_PB_BKR_CLOSE
71 | STATUS_2_SPARE10
72 | HMI_GEN_PB_EMER_RUN
73 | STATUS_2_SPARE12
74 | Standby
75 | AvailableStatus
76 | Emode_HardWire
77 | ExtTankHFL_SD
78 | ExtTankHFL_Alm
79 | ExtTankLFL_SD
80 | ExtTankLFL_Alm
81 | HiFuelFltDiff_SD
82 | HiFuelFltDiff_Alm
83 | HiFuel_SD
84 | HiFuel_Alm
85 | LoFuel_SD
86 | LoFuel_Alm
87 | HiOilLvl_SD
88 | HiOilLvl_Alm
89 | LoOilLvl_SD
90 | LoOilLvl_Alm
91 | HiOilFltDiff_SD
92 | HiOilFltDiff_Alm
93 | LoOilPress_SD
94 | LoOilPress_Alm
95 | HiAirFltDiff_SD
96 | HiAirFltDiff_Alm
97 | HiCoolTemp_SD
98 | HiCoolTemp_Alm
99 | LoCoolTemp_Alm
100 | HiCoolLvl_SD
101 | HiCoolLvl_Alm
102 | LoCoolLvl_SD
103 | LoCoolLvl_Alm
104 | HiBatt_SD
105 | HiBatt_Alm
106 | LoBatt_Alm
107 | HiExhTemp_SD
108 | HiExhTemp_Alm
109 | HiOilTemp_SD
110 | HiOilTemp_Alm
111 | LoOilTemp_SD
112 | LoOilTemp_Alm
113 | Overspeed
114 | Undspeed_SD
115 | Undspeed_Alm
116 | Eng_Estop
117 | Estop_Ovrde
118 | HiRtExhTemp_SD
119 | HiRtExhTemp_Alm
120 | LoRtExhTemp_SD
121 | LoRtExhTemp_Alm
122 | HiLftExhTemp_SD
123 | HiLftExhTemp_Alm
124 | LoLftExhTemp_SD
125 | LoLftExhTemp_Alm
126 | ServInterval_Alm
127 | EMCP_NIA
128 | FuelTankLeak
129 | OverCrank
130 | GEN_VOLT_AB
131 | GEN_VOLT_BC
132 | GEN_VOLT_CA
133 | GEN_VOLT_LL_AVG
134 | GEN_VOLT_AN
135 | GEN_VOLT_BN
136 | GEN_VOLT_CN
137 | GEN_VOLT_LN_AVG
138 | GEN_PHA_AMP
139 | GEN_PHB_AMP
140 | GEN_PHC_AMP
141 | GEN_AVG_AMP
142 | GEN_HZ_FREQ
143 | GEN_KW
144 | GEN_KVAR
145 | GEN_KVA
146 | GEN_PF
147 | GEN_KWH_H
148 | GEN_KWH_L
149 | GEN_KVARH_H
150 | GEN_KVARH_L
151 | GEN_BUS_VOLT_AB
152 | GEN_BUS_VOLT_BC
153 | GEN_BUS_VOLT_CA
154 | GEN_BUS_VOLT_LL_AVG
155 | GEN_BUS_VOLT_AN
156 | GEN_BUS_VOLT_BN
157 | GEN_BUS_VOLT_CN
158 | GEN_BUS_AVG_LN_VOLT
159 | GEN_BUS_REF_HZ
160 | OIL_PRESS
161 | COOLANT_TEMP
162 | ENG_BATT_VOLT
163 | RPM
164 | ENG_HRS_H
165 | ENG_HRS_L
166 | START_STOP_STATE
167 | ANALOG_INPUT_PCNT
168 | ANALOG_INPUT_TEMP
169 | ANALOG_INPUT_PRESS
170 | MAINT_INT_HOURS_REMAIN
171 | MAINT_INT_DAYS_REMAIN
172 | CRANK_ATTEMPTS_H
173 | CRANK_ATTEMPTS_L
174 | EXH_MAN_1_TEMP_DL
175 | EXH_MAN_2_TEMP_DL
176 | INTAKE_MAN_1_TEMP_DL
177 | INTAKE_MAN_2_TEMP_DL
178 | OIL_TEMP_DL
179 | FUEL_TEMP_DL
180 | FUEL_PRESS_DL
181 | CRANKCASE_PRESS_DL
182 | BOOST_PRESS_DL
183 | OIL_FILTER_DIFF_PRESS
184 | FUEL_FILTER_DIFF_PRESS
185 | AIR_FILTER_1_DIFF_PRESS
186 | INSTANT_FUEL_CONSUMPTION_L
187 | ATM_PRESS_DL
188 | MAINT_INT_WEEKS_REMAIN
189 | ENG_ECS_POSITION

## Overall (hidden)
Read / Write
None
Read
Write
Read/Write

## Protocol_Selection (hidden)
Protocol 1 Selection | Protocol 2 Selection
Modbus RTU Master (MM) | BACnet/IP Server (BS)
Modbus TCP/IP Client (MC) | BACnet MS/TP Slave (BMS)

## Mapping (hidden)
Manipulation
None
Mult by 10.0
Mult by 100.0
Mult by 1000.0
Mult by 10000.0
Div by 10.0
Div by 100.0
Div by 1000.0
Div by 10000.0
Extract Bit 0
Extract Bit 1
Extract Bit 2
Extract Bit 3
Extract Bit 4
Extract Bit 5
Extract Bit 6
Extract Bit 7
Extract Bit 8
Extract Bit 9
Extract Bit 10
Extract Bit 11
Extract Bit 12
Extract Bit 13
Extract Bit 14
Extract Bit 15
Extract Bit 16
Extract Bit 17
Extract Bit 18
Extract Bit 19
Extract Bit 20
Extract Bit 21
Extract Bit 22
Extract Bit 23
Extract Bit 24
Extract Bit 25
Extract Bit 26
Extract Bit 27
Extract Bit 28
Extract Bit 29
Extract Bit 30
Extract Bit 31
Extract Bit 32
Extract Bit 33
Extract Bit 34
Extract Bit 35
Extract Bit 36
Extract Bit 37
Extract Bit 38
Extract Bit 39
Extract Bit 40
Extract Bit 41
Extract Bit 42
Extract Bit 43
Extract Bit 44
Extract Bit 45
Extract Bit 46
Extract Bit 47
Extract Bit 48
Extract Bit 49
Extract Bit 50
Extract Bit 51
Extract Bit 52
Extract Bit 53
Extract Bit 54
Extract Bit 55
Extract Bit 56
Extract Bit 57
Extract Bit 58
Extract Bit 59
Extract Bit 60
Extract Bit 61
Extract Bit 62
Extract Bit 63

## Modbus_Configuration (hidden)
Modbus Data Types | Modbus Read Data Types | Modbus Write Data Types | Max Address per Request by Data Type
0x Coil Status (Bit) | 0x Coil Status (Bit) | 0x Coil Status (Bit) | 512
1x Input Status (Bit) | 1x Input Status (Bit) | 4x Holding Register (16 Bit Int) | 125
3x Input Register (16 Bit Int) | 3x Input Register (16 Bit Int) | 4x Holding Register (16 Bit Uint) | 125
3x Input Register (16 Bit Uint) | 3x Input Register (16 Bit Uint) | 4x Holding Register (32 Bit Int) | 62
3x Input Register (32 Bit Int) | 3x Input Register (32 Bit Int) | 4x Holding Register (32 Bit Uint) | 31
3x Input Register (32 Bit Uint) | 3x Input Register (32 Bit Uint) | 4x Holding Register (32 Bit Float)
3x Input Register (32 Bit Float) | 3x Input Register (32 Bit Float) | 4x Holding Register (64 Bit Int)
3x Input Register (64 Bit Int) | 3x Input Register (64 Bit Int) | 4x Holding Register (64 Bit Uint)
3x Input Register (64 Bit Uint) | 3x Input Register (64 Bit Uint) | 4x Holding Register (64 Bit Float)
3x Input Register (64 Bit Float) | 3x Input Register (64 Bit Float)
4x Holding Register (16 Bit Int) | 4x Holding Register (16 Bit Int)
4x Holding Register (16 Bit Uint) | 4x Holding Register (16 Bit Uint)
4x Holding Register (32 Bit Int) | 4x Holding Register (32 Bit Int)
4x Holding Register (32 Bit Uint) | 4x Holding Register (32 Bit Uint)
4x Holding Register (32 Bit Float) | 4x Holding Register (32 Bit Float)
4x Holding Register (64 Bit Int) | 4x Holding Register (64 Bit Int)
4x Holding Register (64 Bit Uint) | 4x Holding Register (64 Bit Uint)
4x Holding Register (64 Bit Float) | 4x Holding Register (64 Bit Float)

## BACnet_Configuration (hidden)
BACnet Object Types | BACnet Read Object Types | BACnet Write Object Types | BACnet Units
Analog Input | Analog Input | Analog Output | %/s: (percent-per-second)
Analog Output | Binary Input | Binary Output | %obs/ft: (percent-obscuration-per-foot)
Binary Input | Character String Value | Character String Value | %obs/m: (percent-obscuration-per-meter)
Binary Output |  |  | /h: (per-hour)
Character String Value |  |  | ang: (degrees-angular)
C/h: (degrees-Celsius-per-hour)
C/m: (degrees-Celsius-per-minute)
C: (degrees-Celsius)
F/h: (degrees-Fahrenheit-per-hour)
F/m: (degrees-Fahrenheit-per-minute)
F: (degrees-Fahrenheit)
K/h: (degrees-Kelvin-per-hour)
K/m: (degrees-Kelvin-per-minute)
K: (degrees-Kelvin)
phase: (degrees-phase)
A/m: (amperes-per-meter)
A/m2: (amperes-per-square-meter)
A: (amperes)
Am2: (ampere-square-meters)
bars
BTU/h: (btus-per-hour)
BTU/lb dry: (btus-per-pound-dry-air)
BTU/lb: (btus-per-pound)
btus
cd/m2: (candelas-per-square-meter)
cd: (candelas)
cm H2O: (centimeters-of-water)
cm Hg: (centimeters-of-mercury)
cm: (centimeters)
cm2: (square-centimeters)
currency 1
currency 10
currency 2
currency 3
currency 4
currency 5
currency 6
currency 7
currency 8
currency 9
cycles-per-hour
cycles-per-minute
days
degrees-days-Celsius
degrees-days-Fahrenheit
deltaF: (delta-degrees-Fahrenheit)
deltaK: (delta-degrees-Kelvin)
F: (farads)
ft/min: (feet-per-minute)
ft/s: (feet-per-second)
ft: (feet)
ft2: (square-feet)
ft3/min: (cubic-feet-per-minute)
ft3/s: (cubic-feet-per-second)
ft3: (cubic-feet)
ftcd: (foot-candles)
g/m: (grams-per-minute)
g/s: (grams-per-second)
gal(uk)/min: (imperial-gallons-per-minute)
gal(uk): (imperial-gallons
gal/min: (us-gallons-per-minute)
gal: (us-gallons)
grams-of-water-per-kilogram-dry-air
H: (henrys)
hours
hp: (horsepower)
hPa: (hectopascals)
hundredths-seconds
Hz: (hertz)
in H2O: (inches-of-water)
in Hg: (inches-of-mercury)
in: (inches)
in2: (square-inches)
J/K: (joules-per-degree-Kelvin)
J/kg dry: (joules-per-kilogram-dry-air)
J/kgK: (joules-per-kilogram-degree-Kelvin)
J/s: (joule-seconds)
J: (joules)
kBTU/h: (kilo-btus-per-hour)
kBTU: (kilo-btus)
kg/h: (kilograms-per-hour)
kg/m: (kilograms-per-minute)
kg/m3: (kilograms-per-cubic-meter)
kg/s: (kilograms-per-second)
kg: (kilograms)
kHz: (kilohertz)
kilohms
kJ/K: (kilojoules-per-degree-Kelvin)
kJ/kg dry: (kilojoules-per-kilogram-dry-air)
kJ/kg: (kilojoules-per-kilogram)
kJ: (kilojoules)
km/hr: (kilometers-per-hour)
kPa: (kilopascals)
kV: (kilovolts)
kVA: (kilovolt-amperes)
kVAr: (kilovolt-amperes-reactive)
kW: (kilowatts)
kWh/m2: (kilowatt-hours-per-square-foot)
kWh/m2: (kilowatt-hours-per-square-meter)
kWh: (kilowatt-hours)
l/hr: (liters-per-hour)
l/min: (liters-per-minute)
l/s: (liters-per-second)
l: (liters)
lb/h: (pounds-mass-per-hour)
lb/m: (pounds-mass-per-minute)
lb/s: (pounds-mass-per-second)
lb: (pounds-mass)
lm: (lumens)
lx: (luxes)
m/hr: (meters-per-hour)
m/min: (meters-per-minute)
m/s/s: (meter-per-second-per-second)
m/s: (meters-per-second)
m: (meters)
m2/N: (square-meters-per-Newton)
m2: (square-meters)
m3/hr: (cubic-meters-per-hour)
m3/min: (cubic-meters-per-minute)
m3/s: (cubic-meters-per-second)
m3: (cubic-meters)
mA: (milliamperes)
mbar: (millibars)
MBTU: (mega-btus)
megohms
MHz: (megahertz)
milliohms
milliseconds
minutes
MJ/K: (megajoules-per-degree-Kelvin)
MJ/ft2: (megajoules-per-square-foot)
MJ/kg dry: (megajoules-per-kilogram-dry-air)
MJ/m2: (megajoules-per-square-meter)
MJ: (megajoules)
mm Hg: (millimeters-of-mercury)
mm/min: (millimeters-per-minute)
mm/s: (millimeters-per-second)
mm: (millimeters)
months
mph.: (miles-per-hour)
MV: (megavolts)
mV: (millivolts)
MVA: (megavolt-amperes)
MVAr: (megavolt-amperes-reactive)
MW: (megawatts)
mW: (milliwatts)
MWh: (megawatt-hours)
N/m: (newtons-per-meter)
N: (newton)
Nm: (newton-meters)
no-units
Ns: (newton-seconds)
ohm-meters
ohms
Pa: (pascals)
per: (percent)
percent-relative-humidity
per-minute
per-second
PF: (power-factor)
ppb: (parts-per-billion)
ppm: (parts-per-million)
psi/F: (psi-per-degree-Fahrenheit)
psi: (pounds-force-per-square-inch)
rad/s: (radians-per-second)
rad: (radians)
rpm: (revolutions-per-minute)
S/m: (siemens-per-meter)
S: (siemens)
seconds
t/h: (tons-per-hour)
T: (teslas)
t: (tons)
th: (ton-hours)
thm: (therms)
TR: (tons-refrigeration)
V/°K: (volts-per-degree-Kelvin)
V/m: (volts-per-meter)
V: (volts)
VA: (volt-amperes)
VAr: (volt-amperes-reactive)
W/ft2: (watts-per-square-foot)
W/m/K: (watts-per-meter-per-degree-Kelvin)
W/m2/K: (watts-per-square-meter-degree-kelvin)
W/m2: (watts-per-square-meter)
W: (watts)
Wb: (webers)
weeks
Wh: (watt-hours)
years