## Sheet1
Device Name: schneider_galaxy_vm
Available Template Part number |  | Description
Schneider_Galaxy_VM_T857 |  | Modbus RTU to BACnet MS/TP
Schneider_Galaxy_VM_T304 |  | Modbus RTU to BACnet/IP
Schneider_Galaxy_VM_T1385 |  | Modbus RTU to Allen-Bradley PLC
Schneider_Galaxy_VM_T295 |  | Modbus TCP/IP to BACnet/IP
Schneider_Galaxy_VM_T858 |  | Modbus TCP/IP to BACnet MS/TP
Schneider_Galaxy_VM_T1386 |  | Modbus TCP/IP to Allen-Bradley PLC
Point | Point Name
1 | Runtime remaining
2 | Estimated charge time
3 | Estimated charge %
4 | Battery Temperature
5 | Battery Power
6 | Battery Voltage
7 | Battery Current
8 | Modular Battery cabinet 1 temp
9 | Modular Battery cabinet 2 temp
10 | Modular Battery cabinet 3 temp
11 | Modular Battery cabinet 4 temp
12 | Modular Battery cabinet 5 temp
13 | Modular Battery cabinet 6 temp
14 | Modular Battery cabinet 7 temp
15 | Modular Battery cabinet 8 temp
16 | Frequency (input)
17 | Voltage L1-2 (input)
18 | Voltage L2-3 (input)
19 | Voltage L3-1 (input)
20 | Current L1 (input)
21 | Current L2 (input)
22 | Current L3 (input)
23 | Active power L1 (input)
24 | Active power L2 (input)
25 | Active power L3 (input)
26 | Apparent power L1 (input)
27 | Apparent power L2 (input)
28 | Apparent power L3 (input)
29 | Total active power (input)
30 | Total apparent power (input)
31 | Voltage L1-N (input)
32 | Voltage L2-N (input)
33 | Voltage L3-N (input)
34 | Maximum RMS CurrentL1(input)Low
35 | Maximum RMS CurrentL1(input)High
36 | Maximum RMS CurrentL2(input)Low
37 | Maximum RMS CurrentL2(input)High
38 | Maximum RMS CurrentL3(input)Low
39 | Maximum RMS CurrentL3(input)High
40 | Power factor L1 (input)
41 | Power factor L2 (input)
42 | Power factor L3 (input)
43 | Frequency (bypass)
44 | Voltage L1-2 (bypass)
45 | Voltage L2-3 (bypass)
46 | Voltage L3-1 (bypass)
47 | Current L1 (bypass)
48 | Current L2 (bypass)
49 | Current L3 (bypass)
50 | Active power L1 (bypass)
51 | Active power L2 (bypass)
52 | Active power L3 (bypass)
53 | Apparent power L1 (bypass)
54 | Apparent power L2 (bypass)
55 | Apparent power L3 (bypass)
56 | Total active power (bypass)
57 | Total apparent power (bypass)
58 | Voltage L1-N (bypass)
59 | Voltage L2-N (bypass)
60 | Voltage L3-N (bypass)
61 | Maximum RMS CurrentL1(bypass)Low
62 | Maximum RMSCurrentL1(bypass)High
63 | Maximum RMS CurrentL2(bypass)Low
64 | Maximum RMSCurrentL2(bypass)High
65 | Maximum RMS CurrentL2(bypass)Low
66 | Maximum RMSCurrentL3(bypass)High
67 | Power factor L1 (bypass)
68 | Power factor L2 (bypass)
69 | Power factor L3 (bypass)
70 | UPS Power Rating
71 | Frequency (output)
72 | Voltage L1-2 (output)
73 | Voltage L2-3 (output)
74 | Voltage L3-1 (output)
75 | Current L1 (output)
76 | Current L2 (output)
77 | Current L3 (output)
78 | Maximum RMS Current L1 (output)
79 | Maximum RMS Current L2 (output)
80 | Maximum RMS Current L3 (output)
81 | Active power L1 (output)
82 | Active power L2 (output)
83 | Active power L3 (output)
84 | Apparent power L1 (output)
85 | Apparent power L2 (output)
86 | Apparent power L3 (output)
87 | Total active power (output)
88 | Total apparent power (output)
89 | Total Output Percent load
90 | Power factor L1 (output)
91 | Power factor L2 (output)
92 | Power factor L3 (output)
93 | Current crest factor L1 (output)
94 | Current crest factor L2 (output)
95 | Current crest factor L3 (output)
96 | Voltage L1-N (output)
97 | Voltage L2-N (output)
98 | Voltage L3-N (output)
99 | Neutral current (output)
100 | Current THD L1 (output)
101 | Current THD L2 (output)
102 | Current THD L3 (output)
103 | UPS Operation Mode
104 | Number of Active Alarms
105 | Highest alarm severity
106 | System Mode
107 | Input kWh
108 | Output kWh
109 | Current L1 (para sys main in)
110 | Current L2 (para sys main in)
111 | Current L3 (para sys main in)
112 | Current L1 (para sys bypass in)
113 | Current L2 (para sys bypass in)
114 | Current L3 (para sys bypass in)
115 | Current L1 (parallel system out)
116 | Current L2 (parallel system out)
117 | Current L3 (parallel system out)
118 | Total apparent power(ParaSysOut)
119 | Total Percent load (para sys)
120 | Number of Battery Modules
121 | Low Battery Alarm Threshold
122 | Battery Type
123 | Battery Solution
124 | Deep Discharge Allowed
125 | Total Battery Capacity
126 | Nominal Output Voltage
127 | Transfer to Static BypassDisable
128 | Flywheel Present
129 | Automatic Battery Disconnect
130 | High Efficiency Mode
131 | UPS operation mode - Battery
132 | BatteryBelowMinAcceptableRuntime
133 | Bypass
134 | UPS operation mode-Battery Test
135 | Battery fault
136 | Informational alarm present
137 | Warning alarm present
138 | Critical alarm present
139 | LostLocalInterfaceToUPSComms
140 | Display communication is lost
141 | Parallel Comms Error PBUS cable1
142 | Parallel Comms Error PBUS cable2
143 | Comms cable termination fault
144 | General parallel system error
145 | Lost parallel redundancy
146 | UPS Op mode-RequestStaticBypass
147 | UPS Op mode - ForcedStaticBypass
148 | UPS Op mode - Maintenance Bypass
149 | Started a self-test
150 | UPS operation mode - Off
151 | UPS operation mode - Initialize
152 | Input phase sequence error
153 | Input frequency fault
154 | Input voltage error
155 | Selftest - Failed
156 | Bypass frequency fault
157 | Bypass phase sequence error
158 | Overload on UPS
159 | Overload on Static bypass switch
160 | Ambient temperature out of range
161 | EPO Switch Activated
162 | Ground fault detected
163 | Bypass voltage error
164 | System locked bypass operation
165 | Batteries are discharging
166 | Charge power is reduced
167 | Battery condition is weak
168 | Battery condition is poor
169 | Ambient temperature high
170 | OverloadUPSDueToHighAmbientTemp
171 | Output frequency fault
172 | Output voltage error
173 | Unit Unit Breaker (UIB) open
174 | Unit Ouput Breaker (UOB) open
175 | MaintenBypassBreaker(MBB)Closed
176 | SystemIsolationBreaker(SIB)open
177 | StaticSwitchInBreaker(SSIB)open
178 | Static bypass switch fault
179 | Static bypass switch warning
180 | High Battery Temperature Level
181 | Low Battery Temperature Level
182 | Battery breaker BB1 open
183 | Battery breaker BB2 open
184 | UPSOperMode-StaticBypassStandby
185 | UPSOperMode-InverterStandby
186 | General UPS settings error
187 | UPS configuration error
188 | Synchronization error
189 | Fan fault
190 | InverterOffDueToRequestByUser
191 | Restricted air flow
192 | Surveillance fault
193 | Charger status
194 | Inverter status
195 | PFC status
196 | Battery status
197 | Technical check recommended
198 | Start-up recommended
199 | Warranty expiring soon
200 | Air filter check recommened
201 | NotEnoughUPSReady2TurnOnInverter
202 | Parallel UPS 1 not present
203 | Parallel UPS 2 not present
204 | Parallel UPS 3 not present
205 | Parallel UPS 4 not present
206 | Parallel UPS 5 not present
207 | Parallel mixed operation mode
208 | System operation mode - Off
209 | SysOpMode-ForcedStaticBypass
210 | SysOpMode-RequestedStaticBypass
211 | SysOpMode-MaintanceBypass
212 | Input missing phase error
213 | Bypass missing phase error
214 | External sync voltage error
215 | External sync phase sequence err
216 | External sync frequency fault
217 | External sync missing phase err
218 | DisplayFirmwareIncompatibility
219 | NMC 1 firmware incompatibility
220 | NMC 2 firmware incompatibility
221 | InverterOutNotPhaseWithBypassIn
222 | Modular battery cabinet 1 fault
223 | Modular battery cabinet 2 fault
224 | Modular battery cabinet 3 fault
225 | Modular battery cabinet 4 fault
226 | Modular battery cabinet 5 fault
227 | Modular battery cabinet 6 fault
228 | Modular battery cabinet 7 fault
229 | Modular battery cabinet 8 fault
230 | ModularBattCabinet1Breaker1Open
231 | ModularBattCabinet1Breaker2Open
232 | ModularBattCabinet2Breaker1Open
233 | ModularBattCabinet2Breaker2Open
234 | ModularBattCabinet3Breaker1Open
235 | ModularBattCabinet3Breaker2Open
236 | ModularBattCabinet4Breaker1Open
237 | ModularBattCabinet4Breaker2Open
238 | ModularBattCabinet5Breaker1Open
239 | ModularBattCabinet5Breaker2Open
240 | ModularBattCabinet6Breaker1Open
241 | ModularBattCabinet6Breaker2Open
242 | ModularBattCabinet7Breaker1Open
243 | ModularBattCabinet7Breaker2Open
244 | ModularBattCabinet8Breaker1Open
245 | ModularBattCabinet8Breaker2Open
246 | Float Charging
247 | Boost Charging
248 | Equalization Charging
249 | Not Charging
250 | Test In Progress
251 | Cyclic Charging
252 | Unit Input Breaker (UIB)
253 | Unit Output Breaker (UOB)
254 | Maintenance Bypass Breaker (MBB)
255 | System Isolation Breaker (SIB)
256 | Static Switch InputBreaker(SSIB)
257 | BatteryBreaker1(ClassicBattery)
258 | BatteryBreaker2(ClassicBattery)

## Overall (hidden)
Read / Write
None
Read
Write
Read/Write

## Protocol_Selection (hidden)
Protocol 1 Selection | Protocol 2 Selection
Modbus RTU Master (MM) | BACnet/IP Server (BS)
Modbus TCP/IP Client (MC) | BACnet MS/TP Slave (BMS)

## Mapping (hidden)
Manipulation
None
Mult by 10.0
Mult by 100.0
Mult by 1000.0
Mult by 10000.0
Div by 10.0
Div by 100.0
Div by 1000.0
Div by 10000.0
Extract Bit 0
Extract Bit 1
Extract Bit 2
Extract Bit 3
Extract Bit 4
Extract Bit 5
Extract Bit 6
Extract Bit 7
Extract Bit 8
Extract Bit 9
Extract Bit 10
Extract Bit 11
Extract Bit 12
Extract Bit 13
Extract Bit 14
Extract Bit 15
Extract Bit 16
Extract Bit 17
Extract Bit 18
Extract Bit 19
Extract Bit 20
Extract Bit 21
Extract Bit 22
Extract Bit 23
Extract Bit 24
Extract Bit 25
Extract Bit 26
Extract Bit 27
Extract Bit 28
Extract Bit 29
Extract Bit 30
Extract Bit 31
Extract Bit 32
Extract Bit 33
Extract Bit 34
Extract Bit 35
Extract Bit 36
Extract Bit 37
Extract Bit 38
Extract Bit 39
Extract Bit 40
Extract Bit 41
Extract Bit 42
Extract Bit 43
Extract Bit 44
Extract Bit 45
Extract Bit 46
Extract Bit 47
Extract Bit 48
Extract Bit 49
Extract Bit 50
Extract Bit 51
Extract Bit 52
Extract Bit 53
Extract Bit 54
Extract Bit 55
Extract Bit 56
Extract Bit 57
Extract Bit 58
Extract Bit 59
Extract Bit 60
Extract Bit 61
Extract Bit 62
Extract Bit 63

## Modbus_Configuration (hidden)
Modbus Data Types | Modbus Read Data Types | Modbus Write Data Types | Max Address per Request by Data Type
0x Coil Status (Bit) | 0x Coil Status (Bit) | 0x Coil Status (Bit) | 512
1x Input Status (Bit) | 1x Input Status (Bit) | 4x Holding Register (16 Bit Int) | 125
3x Input Register (16 Bit Int) | 3x Input Register (16 Bit Int) | 4x Holding Register (16 Bit Uint) | 125
3x Input Register (16 Bit Uint) | 3x Input Register (16 Bit Uint) | 4x Holding Register (32 Bit Int) | 62
3x Input Register (32 Bit Int) | 3x Input Register (32 Bit Int) | 4x Holding Register (32 Bit Uint) | 31
3x Input Register (32 Bit Uint) | 3x Input Register (32 Bit Uint) | 4x Holding Register (32 Bit Float)
3x Input Register (32 Bit Float) | 3x Input Register (32 Bit Float) | 4x Holding Register (64 Bit Int)
3x Input Register (64 Bit Int) | 3x Input Register (64 Bit Int) | 4x Holding Register (64 Bit Uint)
3x Input Register (64 Bit Uint) | 3x Input Register (64 Bit Uint) | 4x Holding Register (64 Bit Float)
3x Input Register (64 Bit Float) | 3x Input Register (64 Bit Float)
4x Holding Register (16 Bit Int) | 4x Holding Register (16 Bit Int)
4x Holding Register (16 Bit Uint) | 4x Holding Register (16 Bit Uint)
4x Holding Register (32 Bit Int) | 4x Holding Register (32 Bit Int)
4x Holding Register (32 Bit Uint) | 4x Holding Register (32 Bit Uint)
4x Holding Register (32 Bit Float) | 4x Holding Register (32 Bit Float)
4x Holding Register (64 Bit Int) | 4x Holding Register (64 Bit Int)
4x Holding Register (64 Bit Uint) | 4x Holding Register (64 Bit Uint)
4x Holding Register (64 Bit Float) | 4x Holding Register (64 Bit Float)

## BACnet_Configuration (hidden)
BACnet Object Types | BACnet Read Object Types | BACnet Write Object Types | BACnet Units
Analog Input | Analog Input | Analog Output | %/s: (percent-per-second)
Analog Output | Binary Input | Binary Output | %obs/ft: (percent-obscuration-per-foot)
Binary Input | Character String Value | Character String Value | %obs/m: (percent-obscuration-per-meter)
Binary Output |  |  | /h: (per-hour)
Character String Value |  |  | ang: (degrees-angular)
C/h: (degrees-Celsius-per-hour)
C/m: (degrees-Celsius-per-minute)
C: (degrees-Celsius)
F/h: (degrees-Fahrenheit-per-hour)
F/m: (degrees-Fahrenheit-per-minute)
F: (degrees-Fahrenheit)
K/h: (degrees-Kelvin-per-hour)
K/m: (degrees-Kelvin-per-minute)
K: (degrees-Kelvin)
phase: (degrees-phase)
A/m: (amperes-per-meter)
A/m2: (amperes-per-square-meter)
A: (amperes)
Am2: (ampere-square-meters)
bars
BTU/h: (btus-per-hour)
BTU/lb dry: (btus-per-pound-dry-air)
BTU/lb: (btus-per-pound)
btus
cd/m2: (candelas-per-square-meter)
cd: (candelas)
cm H2O: (centimeters-of-water)
cm Hg: (centimeters-of-mercury)
cm: (centimeters)
cm2: (square-centimeters)
currency 1
currency 10
currency 2
currency 3
currency 4
currency 5
currency 6
currency 7
currency 8
currency 9
cycles-per-hour
cycles-per-minute
days
degrees-days-Celsius
degrees-days-Fahrenheit
deltaF: (delta-degrees-Fahrenheit)
deltaK: (delta-degrees-Kelvin)
F: (farads)
ft/min: (feet-per-minute)
ft/s: (feet-per-second)
ft: (feet)
ft2: (square-feet)
ft3/min: (cubic-feet-per-minute)
ft3/s: (cubic-feet-per-second)
ft3: (cubic-feet)
ftcd: (foot-candles)
g/m: (grams-per-minute)
g/s: (grams-per-second)
gal(uk)/min: (imperial-gallons-per-minute)
gal(uk): (imperial-gallons
gal/min: (us-gallons-per-minute)
gal: (us-gallons)
grams-of-water-per-kilogram-dry-air
H: (henrys)
hours
hp: (horsepower)
hPa: (hectopascals)
hundredths-seconds
Hz: (hertz)
in H2O: (inches-of-water)
in Hg: (inches-of-mercury)
in: (inches)
in2: (square-inches)
J/K: (joules-per-degree-Kelvin)
J/kg dry: (joules-per-kilogram-dry-air)
J/kgK: (joules-per-kilogram-degree-Kelvin)
J/s: (joule-seconds)
J: (joules)
kBTU/h: (kilo-btus-per-hour)
kBTU: (kilo-btus)
kg/h: (kilograms-per-hour)
kg/m: (kilograms-per-minute)
kg/m3: (kilograms-per-cubic-meter)
kg/s: (kilograms-per-second)
kg: (kilograms)
kHz: (kilohertz)
kilohms
kJ/K: (kilojoules-per-degree-Kelvin)
kJ/kg dry: (kilojoules-per-kilogram-dry-air)
kJ/kg: (kilojoules-per-kilogram)
kJ: (kilojoules)
km/hr: (kilometers-per-hour)
kPa: (kilopascals)
kV: (kilovolts)
kVA: (kilovolt-amperes)
kVAr: (kilovolt-amperes-reactive)
kW: (kilowatts)
kWh/m2: (kilowatt-hours-per-square-foot)
kWh/m2: (kilowatt-hours-per-square-meter)
kWh: (kilowatt-hours)
l/hr: (liters-per-hour)
l/min: (liters-per-minute)
l/s: (liters-per-second)
l: (liters)
lb/h: (pounds-mass-per-hour)
lb/m: (pounds-mass-per-minute)
lb/s: (pounds-mass-per-second)
lb: (pounds-mass)
lm: (lumens)
lx: (luxes)
m/hr: (meters-per-hour)
m/min: (meters-per-minute)
m/s/s: (meter-per-second-per-second)
m/s: (meters-per-second)
m: (meters)
m2/N: (square-meters-per-Newton)
m2: (square-meters)
m3/hr: (cubic-meters-per-hour)
m3/min: (cubic-meters-per-minute)
m3/s: (cubic-meters-per-second)
m3: (cubic-meters)
mA: (milliamperes)
mbar: (millibars)
MBTU: (mega-btus)
megohms
MHz: (megahertz)
milliohms
milliseconds
minutes
MJ/K: (megajoules-per-degree-Kelvin)
MJ/ft2: (megajoules-per-square-foot)
MJ/kg dry: (megajoules-per-kilogram-dry-air)
MJ/m2: (megajoules-per-square-meter)
MJ: (megajoules)
mm Hg: (millimeters-of-mercury)
mm/min: (millimeters-per-minute)
mm/s: (millimeters-per-second)
mm: (millimeters)
months
mph.: (miles-per-hour)
MV: (megavolts)
mV: (millivolts)
MVA: (megavolt-amperes)
MVAr: (megavolt-amperes-reactive)
MW: (megawatts)
mW: (milliwatts)
MWh: (megawatt-hours)
N/m: (newtons-per-meter)
N: (newton)
Nm: (newton-meters)
no-units
Ns: (newton-seconds)
ohm-meters
ohms
Pa: (pascals)
per: (percent)
percent-relative-humidity
per-minute
per-second
PF: (power-factor)
ppb: (parts-per-billion)
ppm: (parts-per-million)
psi/F: (psi-per-degree-Fahrenheit)
psi: (pounds-force-per-square-inch)
rad/s: (radians-per-second)
rad: (radians)
rpm: (revolutions-per-minute)
S/m: (siemens-per-meter)
S: (siemens)
seconds
t/h: (tons-per-hour)
T: (teslas)
t: (tons)
th: (ton-hours)
thm: (therms)
TR: (tons-refrigeration)
V/°K: (volts-per-degree-Kelvin)
V/m: (volts-per-meter)
V: (volts)
VA: (volt-amperes)
VAr: (volt-amperes-reactive)
W/ft2: (watts-per-square-foot)
W/m/K: (watts-per-meter-per-degree-Kelvin)
W/m2/K: (watts-per-square-meter-degree-kelvin)
W/m2: (watts-per-square-meter)
W: (watts)
Wb: (webers)
weeks
Wh: (watt-hours)
years