## Sheet1
Device Name: ABB_ACS310
Available Template Part number |  | Description
Schneider Symmetra PX_T823 |  | Modbus RTU to BACnet MS/TP
Schneider Symmetra PX_T201 |  | Modbus RTU to BACnet/IP
Schneider Symmetra PX_T1359 |  | Modbus RTU to Allen-Bradley PLC
Schneider Symmetra PX_T822 |  | Modbus TCP/IP to BACnet/IP
Schneider Symmetra PX_T824 |  | Modbus TCP/IP to BACnet MS/TP
Schneider Symmetra PX_T1360 |  | Modbus TCP/IP to Allen-Bradley PLC
Point | Point Name
1 | UPS in bypass duefault reg2 or3
2 | UPS in bypass due cmd
3 | UPS return from bypass
4 | UPS bypass mode man bypass
5 | UPS shutdown mode
6 | UPS fault intemp exceed lim
7 | UPS fault UPS in bypass
8 | ON line
9 | ON battery
10 | Overload
11 | Low Battery
12 | Output volt out of range
13 | System not sync
14 | Bypass not in range Freq or volt
15 | System maint bypass
16 | Line quality 00FF ok 0000 bad
17 | Runtime remaining
18 | Batt volt present UPS batt volt
19 | UPS output load full rated watt
20 | Utility input frequency
21 | Phase A utility input voltage
22 | Phase A utility input current
23 | Phase A bypass input voltage
24 | Phase A output voltage
25 | Phase A output current
26 | Phase B utility input voltage
27 | Phase B utility input current
28 | Phase B bypass input voltage
29 | Phase B output voltage
30 | Phase B output current
31 | Phase C utility input voltage
32 | Phase C utility input current
33 | Phase C bypass input voltage
34 | Phase C output voltage
35 | Phase C output current
36 | Exter DC disconnect switch trip
37 | System Power supply card failure
38 | Inter DC disconnect switch trip
39 | Static bypass switch mod fault
40 | Battery current

## Overall (hidden)
Read / Write
None
Read
Write
Read/Write

## Protocol_Selection (hidden)
Protocol 1 Selection | Protocol 2 Selection
Modbus RTU Master (MM) | BACnet/IP Server (BS)
Modbus TCP/IP Client (MC) | BACnet MS/TP Slave (BMS)

## Mapping (hidden)
Manipulation
None
Mult by 10.0
Mult by 100.0
Mult by 1000.0
Mult by 10000.0
Div by 10.0
Div by 100.0
Div by 1000.0
Div by 10000.0
Extract Bit 0
Extract Bit 1
Extract Bit 2
Extract Bit 3
Extract Bit 4
Extract Bit 5
Extract Bit 6
Extract Bit 7
Extract Bit 8
Extract Bit 9
Extract Bit 10
Extract Bit 11
Extract Bit 12
Extract Bit 13
Extract Bit 14
Extract Bit 15
Extract Bit 16
Extract Bit 17
Extract Bit 18
Extract Bit 19
Extract Bit 20
Extract Bit 21
Extract Bit 22
Extract Bit 23
Extract Bit 24
Extract Bit 25
Extract Bit 26
Extract Bit 27
Extract Bit 28
Extract Bit 29
Extract Bit 30
Extract Bit 31
Extract Bit 32
Extract Bit 33
Extract Bit 34
Extract Bit 35
Extract Bit 36
Extract Bit 37
Extract Bit 38
Extract Bit 39
Extract Bit 40
Extract Bit 41
Extract Bit 42
Extract Bit 43
Extract Bit 44
Extract Bit 45
Extract Bit 46
Extract Bit 47
Extract Bit 48
Extract Bit 49
Extract Bit 50
Extract Bit 51
Extract Bit 52
Extract Bit 53
Extract Bit 54
Extract Bit 55
Extract Bit 56
Extract Bit 57
Extract Bit 58
Extract Bit 59
Extract Bit 60
Extract Bit 61
Extract Bit 62
Extract Bit 63

## Modbus_Configuration (hidden)
Modbus Data Types | Modbus Read Data Types | Modbus Write Data Types | Max Address per Request by Data Type
0x Coil Status (Bit) | 0x Coil Status (Bit) | 0x Coil Status (Bit) | 512
1x Input Status (Bit) | 1x Input Status (Bit) | 4x Holding Register (16 Bit Int) | 125
3x Input Register (16 Bit Int) | 3x Input Register (16 Bit Int) | 4x Holding Register (16 Bit Uint) | 125
3x Input Register (16 Bit Uint) | 3x Input Register (16 Bit Uint) | 4x Holding Register (32 Bit Int) | 62
3x Input Register (32 Bit Int) | 3x Input Register (32 Bit Int) | 4x Holding Register (32 Bit Uint) | 31
3x Input Register (32 Bit Uint) | 3x Input Register (32 Bit Uint) | 4x Holding Register (32 Bit Float)
3x Input Register (32 Bit Float) | 3x Input Register (32 Bit Float) | 4x Holding Register (64 Bit Int)
3x Input Register (64 Bit Int) | 3x Input Register (64 Bit Int) | 4x Holding Register (64 Bit Uint)
3x Input Register (64 Bit Uint) | 3x Input Register (64 Bit Uint) | 4x Holding Register (64 Bit Float)
3x Input Register (64 Bit Float) | 3x Input Register (64 Bit Float)
4x Holding Register (16 Bit Int) | 4x Holding Register (16 Bit Int)
4x Holding Register (16 Bit Uint) | 4x Holding Register (16 Bit Uint)
4x Holding Register (32 Bit Int) | 4x Holding Register (32 Bit Int)
4x Holding Register (32 Bit Uint) | 4x Holding Register (32 Bit Uint)
4x Holding Register (32 Bit Float) | 4x Holding Register (32 Bit Float)
4x Holding Register (64 Bit Int) | 4x Holding Register (64 Bit Int)
4x Holding Register (64 Bit Uint) | 4x Holding Register (64 Bit Uint)
4x Holding Register (64 Bit Float) | 4x Holding Register (64 Bit Float)

## BACnet_Configuration (hidden)
BACnet Object Types | BACnet Read Object Types | BACnet Write Object Types | BACnet Units
Analog Input | Analog Input | Analog Output | %/s: (percent-per-second)
Analog Output | Binary Input | Binary Output | %obs/ft: (percent-obscuration-per-foot)
Binary Input | Character String Value | Character String Value | %obs/m: (percent-obscuration-per-meter)
Binary Output |  |  | /h: (per-hour)
Character String Value |  |  | ang: (degrees-angular)
C/h: (degrees-Celsius-per-hour)
C/m: (degrees-Celsius-per-minute)
C: (degrees-Celsius)
F/h: (degrees-Fahrenheit-per-hour)
F/m: (degrees-Fahrenheit-per-minute)
F: (degrees-Fahrenheit)
K/h: (degrees-Kelvin-per-hour)
K/m: (degrees-Kelvin-per-minute)
K: (degrees-Kelvin)
phase: (degrees-phase)
A/m: (amperes-per-meter)
A/m2: (amperes-per-square-meter)
A: (amperes)
Am2: (ampere-square-meters)
bars
BTU/h: (btus-per-hour)
BTU/lb dry: (btus-per-pound-dry-air)
BTU/lb: (btus-per-pound)
btus
cd/m2: (candelas-per-square-meter)
cd: (candelas)
cm H2O: (centimeters-of-water)
cm Hg: (centimeters-of-mercury)
cm: (centimeters)
cm2: (square-centimeters)
currency 1
currency 10
currency 2
currency 3
currency 4
currency 5
currency 6
currency 7
currency 8
currency 9
cycles-per-hour
cycles-per-minute
days
degrees-days-Celsius
degrees-days-Fahrenheit
deltaF: (delta-degrees-Fahrenheit)
deltaK: (delta-degrees-Kelvin)
F: (farads)
ft/min: (feet-per-minute)
ft/s: (feet-per-second)
ft: (feet)
ft2: (square-feet)
ft3/min: (cubic-feet-per-minute)
ft3/s: (cubic-feet-per-second)
ft3: (cubic-feet)
ftcd: (foot-candles)
g/m: (grams-per-minute)
g/s: (grams-per-second)
gal(uk)/min: (imperial-gallons-per-minute)
gal(uk): (imperial-gallons
gal/min: (us-gallons-per-minute)
gal: (us-gallons)
grams-of-water-per-kilogram-dry-air
H: (henrys)
hours
hp: (horsepower)
hPa: (hectopascals)
hundredths-seconds
Hz: (hertz)
in H2O: (inches-of-water)
in Hg: (inches-of-mercury)
in: (inches)
in2: (square-inches)
J/K: (joules-per-degree-Kelvin)
J/kg dry: (joules-per-kilogram-dry-air)
J/kgK: (joules-per-kilogram-degree-Kelvin)
J/s: (joule-seconds)
J: (joules)
kBTU/h: (kilo-btus-per-hour)
kBTU: (kilo-btus)
kg/h: (kilograms-per-hour)
kg/m: (kilograms-per-minute)
kg/m3: (kilograms-per-cubic-meter)
kg/s: (kilograms-per-second)
kg: (kilograms)
kHz: (kilohertz)
kilohms
kJ/K: (kilojoules-per-degree-Kelvin)
kJ/kg dry: (kilojoules-per-kilogram-dry-air)
kJ/kg: (kilojoules-per-kilogram)
kJ: (kilojoules)
km/hr: (kilometers-per-hour)
kPa: (kilopascals)
kV: (kilovolts)
kVA: (kilovolt-amperes)
kVAr: (kilovolt-amperes-reactive)
kW: (kilowatts)
kWh/m2: (kilowatt-hours-per-square-foot)
kWh/m2: (kilowatt-hours-per-square-meter)
kWh: (kilowatt-hours)
l/hr: (liters-per-hour)
l/min: (liters-per-minute)
l/s: (liters-per-second)
l: (liters)
lb/h: (pounds-mass-per-hour)
lb/m: (pounds-mass-per-minute)
lb/s: (pounds-mass-per-second)
lb: (pounds-mass)
lm: (lumens)
lx: (luxes)
m/hr: (meters-per-hour)
m/min: (meters-per-minute)
m/s/s: (meter-per-second-per-second)
m/s: (meters-per-second)
m: (meters)
m2/N: (square-meters-per-Newton)
m2: (square-meters)
m3/hr: (cubic-meters-per-hour)
m3/min: (cubic-meters-per-minute)
m3/s: (cubic-meters-per-second)
m3: (cubic-meters)
mA: (milliamperes)
mbar: (millibars)
MBTU: (mega-btus)
megohms
MHz: (megahertz)
milliohms
milliseconds
minutes
MJ/K: (megajoules-per-degree-Kelvin)
MJ/ft2: (megajoules-per-square-foot)
MJ/kg dry: (megajoules-per-kilogram-dry-air)
MJ/m2: (megajoules-per-square-meter)
MJ: (megajoules)
mm Hg: (millimeters-of-mercury)
mm/min: (millimeters-per-minute)
mm/s: (millimeters-per-second)
mm: (millimeters)
months
mph.: (miles-per-hour)
MV: (megavolts)
mV: (millivolts)
MVA: (megavolt-amperes)
MVAr: (megavolt-amperes-reactive)
MW: (megawatts)
mW: (milliwatts)
MWh: (megawatt-hours)
N/m: (newtons-per-meter)
N: (newton)
Nm: (newton-meters)
no-units
Ns: (newton-seconds)
ohm-meters
ohms
Pa: (pascals)
per: (percent)
percent-relative-humidity
per-minute
per-second
PF: (power-factor)
ppb: (parts-per-billion)
ppm: (parts-per-million)
psi/F: (psi-per-degree-Fahrenheit)
psi: (pounds-force-per-square-inch)
rad/s: (radians-per-second)
rad: (radians)
rpm: (revolutions-per-minute)
S/m: (siemens-per-meter)
S: (siemens)
seconds
t/h: (tons-per-hour)
T: (teslas)
t: (tons)
th: (ton-hours)
thm: (therms)
TR: (tons-refrigeration)
V/°K: (volts-per-degree-Kelvin)
V/m: (volts-per-meter)
V: (volts)
VA: (volt-amperes)
VAr: (volt-amperes-reactive)
W/ft2: (watts-per-square-foot)
W/m/K: (watts-per-meter-per-degree-Kelvin)
W/m2/K: (watts-per-square-meter-degree-kelvin)
W/m2: (watts-per-square-meter)
W: (watts)
Wb: (webers)
weeks
Wh: (watt-hours)
years